## HPM3 ANINNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PNTMODTY | SENSRTYP | PVCHAR | INPTDIR | PVEUHI | PVEULO | PVFORMAT | PVEXEUHI | PVEXEULO | PVCLAMP | LOCUTOFF | TF | PRIMMOD | PVSRCOPT | PVTV | OVERVAL | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | PVALDB | PVHITP | PVHIPR | $HISELCT | PVLOTP | PVHHTP | PVROCPTP | PVROCNTP | BADPVPR | ALENBST | PVLOPR | $LOSELCT | PVLLTP | PVSOURCE | PVLLPR | $LLSELCT | C1 | C2 | TIMEBASE | PVHHPR | $HHSELCT
16190 | PT002364() | HPM | COMPONNT | "PRESSION EAU MOULIN " | "KPA " | " " | " " | " " | DE | 01 | 3 | 1 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 700.0000 | 0.000000 | D1 | 840.0000 | -140.000 | NOCLAMP | -------- | 0.000000
16214 | FI003A310() | HPM | FULL | "DEBIT VAPEUR D'APPOINT " | "KG/H " | " " | " " | " " | DV | 01 | 3 | 1 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 36000.00 | 0.000000 | D0 | 43200.00 | -7200.00 | NOCLAMP | 250.0000 | 0.000000 | -- | ONLYAUTO | 26000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 36000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
16257 | FI003B310() | HPM | FULL | "DEBIT VAP. APPOINT TOTAL" | "KG/H " | " " | " " | " " | DV | 01 | 3 | 2 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 90000.00 | 0.000000 | D0 | 108000.0 | -18000.0 | NOCLAMP | 1000.000 | 0.000000 | -- | ONLYAUTO | 32000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 90000.00 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16303 | PT022324() | HPM | COMPONNT | "PRESSION EAU CHAUFFERIE " | "KPA " | " " | " " | " " | EA | 01 | 3 | 1 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D1 | 1029.000 | -29.0000 | NOCLAMP | -------- | 0.000000
16327 | PT310A310() | HPM | FULL | "PRES.VAP.1310KPA MAITRE " | "KPA " | " " | " " | " " | DV | 01 | 3 | 1 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D1 | 2029.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1050.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1520.000 | LOW | CUTOUT | 700.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16373 | PT310B310() | HPM | FULL | "PRES.VAP.1310KPA MAITRE " | "KPA " | " " | " " | " " | DV | 01 | 3 | 2 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D1 | 2029.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ALL | 1050.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1520.000 | LOW | CUTOUT | 700.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | -------- | AUTO
16420 | PT312A310() | HPM | FULL | "PRESSION VAPEUR 800KPA " | "KPA " | " " | " " | " " | DV | 01 | 3 | 1 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 1700.000 | 0.000000 | D1 | 1729.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 800.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 890.0000 | LOW | CUTOUT | 550.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16466 | PT312B310() | HPM | FULL | "PRESSION VAPEUR 800KPA " | "KPA " | " " | " " | " " | DV | 01 | 3 | 2 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 1700.000 | 0.000000 | D1 | 1729.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 700.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 890.0000 | LOW | CUTOUT | 550.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16512 | PT313A310() | HPM | FULL | "PRESSION VAPEUR 210KPA " | "KPA " | " " | " " | " " | DV | 01 | 3 | 1 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 230.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 275.0000 | LOW | CUTOUT | 190.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16558 | PT313B310() | HPM | FULL | "PRESSION VAPEUR 210KPA " | "KPA " | " " | " " | " " | DV | 01 | 3 | 2 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 210.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 275.0000 | LOW | CUTOUT | 190.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16604 | LT001321() | HPM | COMPONNT | "NIVEAU RESERVOIR MAZOUT " | "% " | " " | " " | " " | MZ | 01 | 3 | 1 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000
16628 | PT060321() | HPM | COMPONNT | "PRES. MAZOUT CHAUDIERES " | "KPA " | " " | " " | " " | MZ | 01 | 3 | 1 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D1 | 3000.000 | -400.000 | NOCLAMP | -------- | 0.000000
16652 | TT804321() | HPM | COMPONNT | "TEMP. MAZOUT CHAUDIERES " | "DEGC " | " " | " " | " " | MZ | 01 | 3 | 1 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 180.0000 | -30.0000 | NOCLAMP | -------- | 0.000000
16676 | LT001A324() | HPM | FULL | "NIVEAU RES. DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 1 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 65.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 70.00000 | LOW | CUTOUT | 48.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16722 | LT001B324() | HPM | FULL | "NIVEAU RES. DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 2 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 60.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 70.00000 | LOW | CUTOUT | 48.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16768 | LT010A324() | HPM | FULL | "NIVEAU RES. CONDENSE " | "% " | " " | " " | " " | EA | 01 | 3 | 1 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 70.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 85.00000 | LOW | CUTOUT | 50.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16814 | LT010B324() | HPM | FULL | "NIVEAU RES. CONDENSE " | "% " | " " | " " | " " | EA | 01 | 3 | 2 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 70.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 85.00000 | LOW | CUTOUT | 50.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16860 | LT011324() | HPM | COMPONNT | "NIV.RES.VIDANGE CONTINUE" | "% " | " " | " " | " " | EA | 01 | 3 | 1 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000
16884 | PT030A324() | HPM | FULL | "PRESSION DEGAZEUR " | "KPA " | " " | " " | " " | EA | 01 | 3 | 1 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 200.0000 | 0.000000 | D1 | 240.0000 | -40.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 100.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 135.0000 | LOW | CUTOUT | 20.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16930 | PT030B324() | HPM | FULL | "PRESSION DEGAZEUR " | "KPA " | " " | " " | " " | EA | 01 | 3 | 2 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 200.0000 | 0.000000 | D1 | 202.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 60.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 135.0000 | LOW | CUTOUT | 20.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
16976 | PT023324() | HPM | COMPONNT | "PRES.EAU ALIM.CHAUDIERES" | "KPA " | " " | " " | " " | EA | 01 | 3 | 1 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 3500.000 | 0.000000 | D1 | 3529.000 | -29.0000 | NOCLAMP | -------- | 0.000000
17000 | PI299310() | HPM | FULL | "PRESSION EAU POTABLE " | "KPA " | " " | " " | " " | AX | 01 | 3 | 5 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D1 | 1200.000 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 482.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 600.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
17043 | PI499310() | HPM | FULL | "PRESSION AIR INSTRUMENT " | "KPA " | " " | " " | " " | AX | 01 | 3 | 5 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D1 | 1029.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 560.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 675.0000 | LOW | CUTOUT | 500.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | 480.0000 |  | NOACTION | CUTOUT
17091 | AI080A321() | HPM | FULL | "SONDE (A) ODEUR MAZOUT " | "PPM " | " " | " " | " " | MZ | 01 | 3 | 5 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D0 | 2400.000 | 0.000000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
17131 | AI080B321() | HPM | FULL | "SONDE (B) ODEUR MAZOUT " | "PPM " | " " | " " | " " | MZ | 01 | 3 | 5 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D0 | 2400.000 | 0.000000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1230.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
17171 | AI080C321() | HPM | FULL | "SONDE (C) ODEUR MAZOUT " | "PPM " | " " | " " | " " | MZ | 01 | 3 | 5 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D0 | 2400.000 | 0.000000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1098.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
17211 | AI080D321() | HPM | FULL | "SONDE (D) ODEUR MAZOUT " | "PPM " | " " | " " | " " | MZ | 01 | 3 | 5 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D0 | 2400.000 | 0.000000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 585.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
17251 | FI003321() | HPM | FULL | "DEBIT VAPEUR RES. MAZOUT" | "KG/H " | " " | " " | " " | MZ | 01 | 3 | 5 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 7500.000 | 0.000000 | D0 | 7529.000 | -29.0000 | NOCLAMP | 375.0000 | 0.000000 | -- | ONLYAUTO | 2250.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
17291 | FI002324() | HPM | FULL | "DEBIT EAU ADOUCISSEURS" | "L/M " | "ADOUCIS." | "EA " | " " | EA | 01 | 3 | 5 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 2250.000 | 0.000000 | D1 | 2279.000 | -29.0000 | CLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1250.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | 0.000000 |  | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
17334 | FI003324() | HPM | FULL | "DEBIT VAPEUR DEGAZEUR " | "KG/H " | " " | " " | " " | EA | 01 | 3 | 5 | 11 | HLAI | 1_5_V | SQRROOT | DIRECT | 23000.00 | 0.000000 | D0 | 23290.00 | -290.000 | CLAMP | 1150.000 | 0.100000 | -- | ONLYAUTO | 16500.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 22000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
17377 | FI020324() | HPM | FULL | "DEBIT EAU CHAUDIERES " | "L/M " | " " | " " | " " | EA | 01 | 3 | 5 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 7500.000 | 0.000000 | D1 | 9000.000 | -1500.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 3800.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
17417 | FT080324() | HPM | COMPONNT | "DEBIT PHOSPHATE " | "ml / min" | " " | " " | " " | EA | 01 | 3 | 5 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 34.15000 | 0.000000 | D2 | 40.00000 | -5.66000 | CLAMP | 0.000000 | 0.000000
17441 | FT081324() | HPM | COMPONNT | "DEBIT SULPHITE " | "ml / min" | " " | " " | " " | EA | 01 | 3 | 5 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 34.15000 | 0.000000 | D2 | 37.00000 | -3.33000 | NOCLAMP | -------- | 0.000000
17465 | FT082324() | HPM | COMPONNT | "DEBIT AMINE+PASSIVATEUR " | "ml / min" | " " | " " | " " | EA | 01 | 3 | 5 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 34.15000 | 0.000000 | D2 | 37.00000 | -5.66000 | NOCLAMP | -------- | 0.000000
17489 | FI231324() | HPM | FULL | "DEBIT EAU ADOUCI. #1 " | "L/M " | "ADOUCI#1" | "EA " | " " | EA | 01 | 3 | 5 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 2250.000 | 0.000000 | D1 | 2279.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 700.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1500.000 | LOW | CUTOUT | 50.00000 | -------- | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | --------
17535 | FI232324() | HPM | FULL | "DEBIT EAU ADOUCI. #2 " | "L/M " | "ADOUCI#2" | "EA " | " " | EA | 01 | 3 | 6 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 2250.000 | 0.000000 | D1 | 2279.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 740.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1500.000 | LOW | CUTOUT | 50.00000 | -------- | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | --------
17581 | FI233324() | HPM | FULL | "DEBIT EAU ADOUCI. #3 " | "L/M " | "ADOUCI#3" | "EA " | " " | EA | 01 | 3 | 6 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 2250.000 | 0.000000 | D1 | 2279.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 740.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1500.000 | LOW | CUTOUT | 50.00000 | -------- | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | --------
17627 | TI800324() | HPM | FULL | "TEMP. EAU ADOUCISSEURS" | "DEGC " | "ADOUCIS." | "EA " | " " | EA | 01 | 3 | 6 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 50.00000 | 0.000000 | D1 | 60.00000 | -10.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 20.10000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
17667 | FI753310() | HPM | FULL | "DEBIT E.F. CHAUFFERIE " | "L/M " | " " | " " | " " | DE | 01 | 3 | 5 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | DISABLE
17707 | PI021364() | HPM | FULL | "PRESSION E.F. MOULIN " | "KPA " | " " | " " | " " | DE | 01 | 3 | 5 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D1 | 1029.000 | -29.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 440.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 560.0000 | LOW | CUTOUT | 350.0000 | -------- | -------- | -------- | LOW | DISABLE | LOW | CUTOUT | --------
18095 | LT093311() | HPM | COMPONNT | "NIVEAU CHUTE A ECORCES " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
18173 | FT050318() | HPM | FULL | "DEBIT GAZ CHAUDIERE #8" | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 6 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 0.100000 | 0.100000 | HOURS
18213 | FT050311() | HPM | FULL | "DEBIT GAZ CHAUDIERE #1" | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 4 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 1.000000 | 1.000000 | HOURS
18253 | FT040282() | HPM | FULL | "DEBIT GAZ COUCHEUSE 8 " | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 1 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 1.000000 | 1.000000 | HOURS
18293 | FT040290() | HPM | FULL | "DEBIT GAZ COUCHEUSE 9 " | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 2 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 1.000000 | 1.000000 | HOURS
18333 | FT040300() | HPM | FULL | "DEBIT GAZ ENTREPOT " | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 3 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 0.010000 | 0.010000 | HOURS
18373 | FT050319() | HPM | FULL | "DEBIT GAZ CHAUDIERE #9" | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 7 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 1.000000 | 1.000000 | HOURS
18413 | FT790500() | HPM | FULL | "DEBIT GAZ MP10 " | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 16 | 1 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 6000.000 | -1000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 1.000000 | 1.000000 | HOURS
18619 | FT201289() | HPM | FULL | "DEBIT GAZ USINE " | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 8 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -100.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 1.000000 | 1.000000 | HOURS
18659 | FI250324() | HPM | FULL | "DEBIT EAU FILTRE SUD " | "L/M " | " " | " " | " " | EA | 01 | 3 | 6 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 4000.000 | 0.000000 | D1 | 4800.000 | -800.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 2000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
18699 | FI260324() | HPM | FULL | "DEBIT EAU FILTRE NORD " | "L/M " | " " | " " | " " | EA | 01 | 3 | 6 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 4000.000 | 0.000000 | D1 | 4800.000 | -800.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 2200.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
18757 | PI021324() | HPM | FULL | "PRES. ENTREE FILTRES " | "kPA " | " " | "EA " | " " | EA | 01 | 3 | 10 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D0 | 1200.000 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 700.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 725.0000 | NOACTION | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
18977 | LT001311() | HPM | FULL | "NIVEAU CHAUDIERE #1" | "mmH2O " | " " | "C1 " | " " | C1 | 01 | 3 | 1 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | -400.000 | D1 | 480.0000 | -480.000 | NOCLAMP | -------- | 0.040000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19017 | FT004311() | HPM | FULL | "DEBIT AIR BRULEUR #2 " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 9 | HLAI | 1_5_V | SQRROOT | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19057 | FT002311() | HPM | FULL | "DEBIT EAU CHAUDIERE #1" | "Kg/h " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 68000.00 | 0.000000 | D0 | 100000.0 | -17000.0 | NOCLAMP | 0.000000 | 0.001800 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19097 | FT005311() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #1" | "m3/h " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 493.0000 | 0.000000 | D0 | 550.0000 | -50.0000 | NOCLAMP | 0.000000 | 0.000000
19121 | ST009311() | HPM | COMPONNT | "VITESSE CONV. A VIS " | "RPM " | " " | "SE " | " " | SE | 01 | 3 | 2 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 18.00000 | 0.000000 | D1 | 22.00000 | -4.00000 | NOCLAMP | -------- | 0.100000
19145 | LT012311() | HPM | COMPONNT | "NIV. CHAMBRE DE CONTACT " | "% " | " " | "LG " | " " | LG | 01 | 3 | 2 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.100000
19169 | FI020311() | HPM | FULL | "DEBIT EAU CHAUDIERE #1" | "L/M " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 1515.000 | 0.000000 | D1 | 1815.000 | -300.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 850.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19209 | PI030311() | HPM | FULL | "PRES.VAPEUR CHAUDIERE #1" | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 2070.000 | 0.000000 | D0 | 2500.000 | -500.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1400.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1550.000 | HIGH | CUTOUT | 850.0000 | -------- | -------- | -------- | LOW | ENABLE | HIGH | CUTOUT | --------
19255 | FT040A311() | HPM | FULL | "DEBIT AIR FORCE NORD " | "m3/m " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 15 | HLAI | 1_5_V | SQRROOT | DIRECT | 800.0000 | 0.000000 | D0 | 1000.000 | -100.000 | NOCLAMP | -------- | 0.100000 | -- | ONLYAUTO | 650.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | 0.200000 |  | -------- | -------- | HIGH | ENABLE | NOACTION | CUTOUT | 0.140000 |  | HIGH | CUTOUT
19300 | FT040B311() | HPM | FULL | "DEBIT AIR FORCE SUD " | "m3/m " | " " | "C1 " | " " | C1 | 01 | 3 | 2 | 16 | HLAI | 1_5_V | SQRROOT | DIRECT | 800.0000 | 0.000000 | D0 | 1000.000 | -100.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 575.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | 0.200000 |  | -------- | -------- | NOACTION | ENABLE | NOACTION | CUTOUT | --------
19343 | FT003311() | HPM | FULL | "DEBIT VAPEUR CHAUD. #1 " | "Kg/h " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 1 | HLAI | 1_5_V | SQRROOT | DIRECT | 68000.00 | 0.000000 | D0 | 90000.00 | -10000.0 | NOCLAMP | 3400.000 | 0.000000 | -- | ONLYAUTO | 60000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 60000.00 | HIGH | CUTOUT | -------- | 65000.00 | -------- | -------- | LOW | ENABLE | [9 empty] | EMERGNCY | CUTOUT
19388 | PT041A311() | HPM | COMPONNT | "PRESSION AIR FORCE " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 3.000000 | 0.000000 | D2 | 3.600000 | -0.60000 | NOCLAMP | -------- | 0.000000
19412 | PI041B311() | HPM | FULL | "PRESSION AIR SOUS GRILLE" | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 1.250000 | 0.000000 | D2 | 1.500000 | -0.25000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.500000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19452 | PT042311() | HPM | FULL | "PRESSION FOYER " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 0.075000 | -0.07500 | D3 | 0.150000 | -0.10000 | NOCLAMP | -------- | 0.100000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19492 | PT043311() | HPM | COMPONNT | "PRESSION AIR SUR GRILLE " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | -------- | 0.100000
19516 | FI044A311() | HPM | FULL | "DEBIT AIR SECOND. ARR." | "m3/m " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 7 | HLAI | 1_5_V | SQRROOT | DIRECT | 500.0000 | 0.000000 | D1 | 600.0000 | -100.000 | NOCLAMP | -------- | 0.100000 | -- | ONLYAUTO | 90.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 450.0000 | HIGH | CUTOUT | -100.000 | -------- | -------- | -------- | LOW | ENABLE | HIGH | CUTOUT | --------
19562 | FI044B311() | HPM | FULL | "DEBIT AIR SECOND.AVANT" | "m3/m " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 8 | HLAI | 1_5_V | SQRROOT | DIRECT | 250.0000 | 0.000000 | D1 | 300.0000 | -25.0000 | NOCLAMP | -------- | 0.100000 | -- | ONLYAUTO | 75.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 250.0000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
19636 | PI058311() | HPM | FULL | "PRESSION GAZ BRULEURS " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 90.00000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 30.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 86.00000 | LOW | CUTOUT | 3.500000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
19682 | AT080311() | HPM | COMPONNT | "CONTROLE O2 COMBUSTION " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 21.00000 | 0.000000 | D1 | 25.00000 | -4.00000 | NOCLAMP | -------- | 0.000000
19706 | AI081311() | HPM | FULL | "O2 SORTIE RECHAUFFEUR " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 20.00000 | 0.000000 | D2 | 24.00000 | -4.00000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 8.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | 3.500000 |  | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | --------
19749 | AI082311() | HPM | FULL | "CO GAZ DE COMBUSTION " | "PPM " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D0 | 2200.000 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 500.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19789 | AI083311() | HPM | FULL | "OPACITE CHEMINEE CH1" | "% " | " " | "LG " | " " | LG | 01 | 3 | 3 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
19829 | TI818311() | HPM | FULL | "TEMPERATURE FOYER " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 8 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 1600.000 | 600.0000 | D0 | 1700.000 | 500.0000 | NOCLAMP | -------- | 0.050000 | -- | ONLYAUTO | 1050.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1350.000 | LOW | CUTOUT | 500.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
19875 | FT006311() | HPM | COMPONNT | "DEBIT HUILE CHAUDIERE #1" | "Kg/h " | " " | "C1 " | " " | C1 | 01 | 3 | 6 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 4080.000 | 0.000000 | D0 | 5000.000 | -1000.00 | NOCLAMP | 200.0000 | 0.000000
19899 | AT008311() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #1 " | "uMHOS " | " " | "C1 " | " " | C1 | 01 | 3 | 6 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 5000.000 | 0.000000 | D0 | 6000.000 | -1000.00 | NOCLAMP | -------- | 0.000000
19923 | LI013311() | HPM | FULL | "NIVEAU SILO ECORCES " | "% " | " " | "SE " | " " | SE | 01 | 3 | 6 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 90.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 92.00000 | LOW | CUTOUT | -------- | 93.00000 | -------- | -------- | LOW | ENABLE | [9 empty] | NOACTION | CUTOUT
19968 | PT031311() | HPM | COMPONNT | "PRES. VAPEUR ATOMISANTE " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 6 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 1375.000 | 0.000000 | D1 | 1700.000 | -300.000 | NOCLAMP | -------- | 0.000000
19992 | PI046A311() | HPM | FULL | "PRES. ENTREE RECHAUFFEUR" | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 6 | 12 | HLAI | 1_5_V | LINEAR | REVERSE | 0.000000 | -2.00000 | D2 | 0.400000 | -2.40000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -0.30000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -2.00000 |  | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20035 | PI046B311() | HPM | FULL | "PRES. SORTIE RECHAUFFEUR" | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 6 | 13 | HLAI | 1_5_V | LINEAR | REVERSE | 0.000000 | -3.00000 | D2 | 0.600000 | -3.60000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -1.08000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 0.000000 | NOACTION | CUTOUT | -3.00000 | -------- | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | --------
20081 | PI047311() | HPM | FULL | "PRESSION AIR VENT.HUMIDE" | "Kpa " | " " | "LG " | " " | LG | 01 | 3 | 6 | 14 | HLAI | 1_5_V | LINEAR | REVERSE | 0.000000 | -5.00000 | D2 | 0.400000 | -6.00000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -1.60000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 0.000000 | LOW | CUTOUT | -6.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20127 | PI048311() | HPM | FULL | "PRESSION AIR VENT.INDUIT" | "Kpa " | " " | "LG " | " " | LG | 01 | 3 | 6 | 15 | HLAI | 1_5_V | LINEAR | REVERSE | 0.000000 | -5.00000 | D2 | 0.600000 | -6.00000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -0.10000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 0.000000 | LOW | CUTOUT | -5.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20173 | PI049311() | HPM | FULL | "PRESSION AIR COMBUSTION " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 6 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 2.500000 | 0.000000 | D2 | 3.000000 | -0.50000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.150000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
20213 | PI060311() | HPM | FULL | "PRESSION HUILE CH#1 " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 1034.000 | 0.000000 | D0 | 1250.000 | -250.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 620.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
20253 | LI100311() | HPM | FULL | "NIVEAU HUILE USEE " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 80.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 70.00000 | HIGH | CUTOUT | 15.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20299 | TI800311() | HPM | FULL | "ENTREE AIR RECHAUFFEUR " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 65.00000 | 0.000000 | D1 | 72.00000 | -7.00000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 37.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 65.00000 | LOW | CUTOUT | 5.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20345 | TI801311() | HPM | FULL | "SORTIE AIR RECHAUFFEUR " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 425.0000 | 0.000000 | D1 | 510.0000 | -85.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 275.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 400.0000 | LOW | CUTOUT | 150.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20391 | TI802311() | HPM | FULL | "ENTREE GAZ RECHAUFEUR " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 425.0000 | 0.000000 | D1 | 510.0000 | -85.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 432.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 440.0000 | LOW | CUTOUT | 120.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20437 | TI803311() | HPM | FULL | "SORTIE GAZ RECHAUFEUR " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 425.0000 | 0.000000 | D1 | 510.0000 | -85.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 217.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 290.0000 | LOW | CUTOUT | 90.00000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20483 | TI804311() | HPM | FULL | "TEMPERATURE MAZOUT CH#1 " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 180.0000 | -30.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 121.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 121.0000 | HIGH | CUTOUT | 93.00000 | -------- | -------- | -------- | LOW | ENABLE | HIGH | CUTOUT | --------
20529 | TI807311() | HPM | FULL | "TEMP. TUBES CHAUDIERE #1" | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 537.0000 | 0.000000 | D1 | 650.0000 | -110.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 342.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
20569 | TI810311() | HPM | FULL | "TEMP. GRILLE AVANT BAS " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 345.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 333.0000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20615 | TI811311() | HPM | FULL | "TEMP. GRILLE AVANT HAUT " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 295.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 333.0000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20661 | TI812311() | HPM | FULL | "TEMP.GRILLE CENTRE AVANT" | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 250.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 340.0000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | NOACTION | ENABLE | LOW | CUTOUT | --------
20707 | TI813311() | HPM | FULL | "TEMP.GRILLE CENTRE ARR. " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 234.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 333.0000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20753 | TI814311() | HPM | FULL | "TEMP.GRILLE ARRIERE BAS " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 232.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 333.0000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20799 | TI815311() | HPM | FULL | "TEMP.GRILLE ARRIERE HAUT" | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 224.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 333.0000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20845 | TI816A311() | HPM | FULL | "TEMP. AIR BRULEUR NORD" | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 7 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 537.0000 | -28.9000 | D1 | 600.0000 | -100.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 235.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 290.0000 | HIGH | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20891 | TI816B311() | HPM | FULL | "TEMP. AIR BRULEUR SUD " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 8 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 537.0000 | -28.9000 | D1 | 600.0000 | -100.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 264.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 290.0000 | HIGH | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
20937 | ST922311() | HPM | COMPONNT | "VITESSE CONV.CENDRES" | "m/m " | " " | "LG " | " " | LG | 01 | 3 | 8 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 3.050000 | 0.000000 | D2 | 4.000000 | -0.60000 | NOCLAMP | -------- | 0.000000
21185 | AI088311() | HPM | FULL | "HUMIDITE ECORCES CH#1" | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 50.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
21243 | PT052311() | HPM | FULL | "PRESSION GAZ NATUREL " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 520.0000 | 0.000000 | D1 | 624.0000 | -104.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
21297 | PI900311() | HPM | FULL | "PRES. HUILE CONV. A VIS " | "Kpa " | " " | "SE " | " " | SE | 01 | 3 | 8 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 13800.00 | 0.000000 | D0 | 14200.00 | -1200.00 | NOCLAMP | -------- | 0.100000 | -- | ONLYAUTO | 10000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 12860.00 | HIGH | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
21343 | I41_5N311() | HPM | FULL | "COURANT GRILLE MOBIL" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 4 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 175.0000 | -25.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 70.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 69.00000 | LOW | CUTOUT | 20.00000 | -------- | -------- | -------- | LOW | ENABLE | EMERGNCY | CUTOUT | --------
21407 | TT822311() | HPM | FULL | "TEMPERATURE GAZ NATUREL " | "degC " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 50.00000 | 0.000000 | D1 | 60.00000 | -10.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
21513 | PI498310() | HPM | FULL | "PRESSION AIR MOULIN " | "KPA " | " " | " " | " " | AX | 01 | 3 | 8 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D1 | 1200.000 | -200.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 530.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 700.0000 | LOW | CUTOUT | 480.0000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | 450.0000 |  | HIGH | CUTOUT
21561 | PT499303() | HPM | COMPONNT | "AIR INST. EMBALLEUSE " | "kPa " | " " | " " | " " | AX | 01 | 3 | 9 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D1 | 1200.000 | -200.000 | NOCLAMP | -------- | 0.000000
21665 | FI003201() | HPM | FULL | "DEBIT VAPEUR MOULIN A " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 109000.0 | 0.000000 | D0 | 130800.0 | -21800.0 | NOCLAMP | 2725.000 | 0.000000 | -- | ONLYAUTO | 26000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 50000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
21708 | FI003205() | HPM | FULL | "DEBIT VAPEUR MOULIN B " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 90600.00 | 0.000000 | D0 | 108720.0 | -18120.0 | NOCLAMP | 2265.000 | 0.000000 | -- | ONLYAUTO | 15000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 65000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
21751 | FI003270() | HPM | FULL | "DEBIT VAPEUR MP7 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 50000.00 | 0.000000 | D0 | 60000.00 | -10000.0 | NOCLAMP | 2500.000 | 0.000000 | -- | ONLYAUTO | 29000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 32000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | DISABLE
21794 | FI003280() | HPM | FULL | "DEBIT VAPEUR COUCH.SUPER" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 5455.000 | 0.000000 | D0 | 6000.000 | -400.000 | NOCLAMP | 675.0000 | 0.000000 | -- | ONLYAUTO | 1500.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 5000.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | DISABLE
21837 | FI003281() | HPM | FULL | "DEBIT VAPEUR CUISINE " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 10800.00 | 0.000000 | D0 | 12960.00 | -2160.00 | NOCLAMP | 540.0000 | 0.000000 | -- | ONLYAUTO | 3000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
21880 | FI376213() | HPM | FULL | "DEBIT BOITE VAPEUR MP1 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 2260.000 | 0.000000 | D0 | 2712.000 | -452.000 | NOCLAMP | 113.0000 | 0.000000 | -- | ONLYAUTO | 2500.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
21920 | FI376273() | HPM | FULL | "DEBIT BOITE VAPEUR MP7 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 12 | HLAI | 1_5_V | SQRROOT | DIRECT | 6000.000 | 0.000000 | D0 | 7200.000 | -1200.00 | NOCLAMP | 300.0000 | 0.000000 | -- | ONLYAUTO | 3330.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
21960 | FI402254() | HPM | FULL | "DEBIT VAPEUR 210 KPA MP5" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 18150.00 | 0.000000 | D0 | 21780.00 | -3630.00 | NOCLAMP | 907.0000 | 0.000000 | -- | ONLYAUTO | 11500.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 18000.00 | NOACTION | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22003 | FI402274() | HPM | FULL | "DEBIT VAPEUR 210 KPA MP7" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 14 | HLAI | 1_5_V | SQRROOT | DIRECT | 45359.00 | 0.000000 | D0 | 54420.00 | -9070.00 | NOCLAMP | 2268.000 | 0.000000 | -- | ONLYAUTO | 15000.00 | 25 | -- | NONE | NONE | 0 | 0 | TWO | 45000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22046 | FI404274() | HPM | FULL | "DEBIT VAPEUR THERMO MP7 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 15 | HLAI | 1_5_V | SQRROOT | DIRECT | 56700.00 | 0.000000 | D0 | 68040.00 | -11340.0 | NOCLAMP | 2835.000 | 0.000000 | -- | ONLYAUTO | 7000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
22086 | FI426264() | HPM | FULL | "DEBIT VAPEUR 800 KPA MP6" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 8 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 135000.0 | 0.000000 | D0 | 162000.0 | -27000.0 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
22126 | FI427214() | HPM | FULL | "DEBIT VAPEUR 210 KPA MP1" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 1 | HLAI | 1_5_V | SQRROOT | DIRECT | 13600.00 | 0.000000 | D0 | 16320.00 | -2720.00 | CLAMP | 680.0000 | 0.000000 | -- | ONLYAUTO | 8000.000 | 25 | -- | NONE | NONE | 0 | 0 | FIVE | 13000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22169 | FI402224() | HPM | FULL | "DEBIT VAPEUR 210 KPA MP2" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 2 | HLAI | 1_5_V | SQRROOT | DIRECT | 18100.00 | 0.000000 | D0 | 21720.00 | -3620.00 | NOCLAMP | 905.0000 | 0.000000 | -- | ONLYAUTO | 11000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 18000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22212 | FI427244() | HPM | FULL | "DEBIT VAPEUR 210 KPA MP4" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 3 | HLAI | 1_5_V | SQRROOT | DIRECT | 13600.00 | 0.000000 | D0 | 16320.00 | -2720.00 | NOCLAMP | 680.0000 | 0.000000 | -- | ONLYAUTO | 8500.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 13000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22255 | FI427264() | HPM | FULL | "DEBIT VAPEUR 210 KPA MP6" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 4 | HLAI | 1_5_V | SQRROOT | DIRECT | 18140.00 | 0.000000 | D0 | 21768.00 | -3628.00 | NOCLAMP | 907.0000 | 0.000000 | -- | ONLYAUTO | 9200.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 18000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22298 | FI428214() | HPM | FULL | "DEBIT VAPEUR THERMO MP1 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 5 | HLAI | 1_5_V | SQRROOT | DIRECT | 4530.000 | 0.000000 | D0 | 5436.000 | -906.000 | NOCLAMP | 227.0000 | 0.000000 | -- | ONLYAUTO | 1160.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
22338 | FI428264() | HPM | FULL | "DEBIT VAPEUR THERMO MP6 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 6 | HLAI | 1_5_V | SQRROOT | DIRECT | 6800.000 | 0.000000 | D0 | 8160.000 | -1360.00 | NOCLAMP | 340.0000 | 0.000000 | -- | ONLYAUTO | 5200.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 6800.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22381 | FI494274() | HPM | FULL | "DEBIT VAPEUR 210 KPA AUX" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 13600.00 | 0.000000 | D0 | 16320.00 | -2720.00 | NOCLAMP | 680.0000 | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | NOACTION | ENABLE
22421 | FI943500() | HPM | FULL | "DEBIT VAPEUR MP10 " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 90000.00 | 0.000000 | D0 | 108000.0 | -18000.0 | NOCLAMP | 4500.000 | 0.000000 | -- | ONLYAUTO | 62000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 75000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22464 | FI003140() | HPM | FULL | "DEBIT VAPEUR TMP " | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 34000.00 | 0.000000 | D0 | 40800.00 | -6800.00 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 10000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 25000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22507 | FI753120() | HPM | FULL | "DEBIT E.F.MP1234 TAMA C8" | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 20000.00 | 0.000000 | D0 | 24000.00 | -4000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
22547 | FI753121() | HPM | FULL | "DEBIT E.F. DEF A_B TAMA" | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | DISABLE
22590 | FI753122() | HPM | FULL | "DEBIT E.F. TAMISAGE A " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | DISABLE
22633 | FI753A130() | HPM | FULL | "DEBIT E.F.MP567 TAMB C9 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22676 | FI753B130() | HPM | FULL | "DEBIT E.F.MP567 TAMB C9 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 20000.00 | 0.000000 | D0 | 24000.00 | -4000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 20000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22719 | FI753C130() | HPM | FULL | "DEBIT E.F.MP56 COUCH.9 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22762 | FI753A140() | HPM | FULL | "DEBIT E.F. TMP L1_L2_L3" | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 30000.00 | 0.000000 | D0 | 36000.00 | -6000.00 | CLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 32000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22805 | FI753B140() | HPM | FULL | "DEBIT E.F. TMP L4_L5 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 14000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 14000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22848 | FI753A151() | HPM | FULL | "DEBIT E.F. KRAFT_GL_AMI" | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
22891 | FI753B151() | HPM | FULL | "DEBIT E.F. KRAFT_GL_AMI" | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 10000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
22934 | FI753270() | HPM | FULL | "DEBIT E.F. MP7 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 15000.00 | 0.000000 | D0 | 18000.00 | -3000.00 | NOCLAMP | -------- | 0.000000 | -- | ALL | 6400.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 15000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | DISABLE |  |  |  | AUTO
22978 | FI753280() | HPM | FULL | "DEBIT E.F. COUCHEUSE 8 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D0 | 2400.000 | -400.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 2000.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
23021 | FI753A290() | HPM | FULL | "DEBIT E.F. COUCHEUSE 9 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 1500.000 | 0.000000 | D0 | 1800.000 | -300.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1500.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
23064 | FI753B290() | HPM | FULL | "DEBIT E.F. COUCHEUSE 9 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 1500.000 | 0.000000 | D0 | 1800.000 | -300.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1500.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
23107 | FI753500() | HPM | FULL | "DEBIT E.F. MP10 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 10 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 15000.00 | 0.000000 | D0 | 17000.00 | -2726.00 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 8000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23147 | FI427500() | HPM | FULL | "DEBIT VAPEUR 210KPA MP10" | "Kg/h " | " " | "DV " | " " | DV | 01 | 3 | 9 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 58967.00 | 0.000000 | D0 | 64700.00 | -6800.00 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 37000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 57000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | DISABLE
23190 | FT050317() | HPM | FULL | "DEBIT GAZ CHAUDIERE #7" | "m3/h " | " " | "GN " | " " | GN | 01 | 3 | 15 | 5 | PI |  |  |  | 5000.000 | 0.000000 | D1 | 10000.00 | -100.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | -------- | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE | [6 empty] | 0.100000 | 0.100000 | HOURS
23230 | SI093311() | HPM | FULL | "VITESSE CONV. #224 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 45.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23306 | SIYYY311() | HPM | COMPONNT | "VITESSE YYY " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
23428 | SI098311() | HPM | COMPONNT | "VITESSE GRILLE MOBIL" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 4 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
23452 | SI094311() | HPM | COMPONNT | "VITESSE CONV. 231 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
23476 | SI095311() | HPM | COMPONNT | "VITESSE CONV. 232 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
23500 | SI096311() | HPM | COMPONNT | "VITESSE CONV. 233 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
23524 | SI097311() | HPM | COMPONNT | "VITESSE CONV. 234 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | -------- | 0.000000
23566 | I42_5N311() | HPM | FULL | "COURANT YYY " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 175.0000 | -25.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 110.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23606 | I43_5N311() | HPM | FULL | "COURANT CONV. 231 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 175.0000 | -25.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23646 | I44_5N311() | HPM | FULL | "COURANT CONV. 232 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 175.0000 | -25.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23686 | I45_5N311() | HPM | FULL | "COURANT CONV. 233 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 175.0000 | -25.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 100.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 60.00000 | NOACTION | CUTOUT | -------- | -------- | -------- | -------- | LOW | ENABLE
23729 | I46_5N311() | HPM | FULL | "COURANT CONV. 234 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 4 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 175.0000 | -25.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 90.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23787 | PT400311() | HPM | FULL | "PRESSION AIRLAVEUR A GAZ" | "KPA " | " " | "LG " | " " | LG | 01 | 3 | 4 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 1034.000 | 0.000000 | D0 | 1250.000 | -15.0000 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 540.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23827 | FT450311() | HPM | COMPONNT | "DEBIT AIR DIST.ECORCES" | "m3/m " | " " | "C1 " | " " | C1 | 01 | 3 | 1 | 16 | HLAI | 1_5_V | SQRROOT | DIRECT | 99.00000 | 0.000000 | D1 | 110.0000 | -10.0000 | NOCLAMP | -------- | 0.250000
23869 | PI045311() | HPM | FULL | "PRES. AIR DIST.ECORCES" | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 3 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 12.50000 | 0.000000 | D1 | 15.00000 | -2.50000 | NOCLAMP | -------- | 0.100000 | -- | ONLYAUTO | 5.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
23909 | AI004B324() | HPM | FULL | "DURETE EAU SORTIE DEGAZ" | "PPM " | " " | "EA " | " " | EA | 01 | 3 | 9 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 0.500000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
23952 | AI004A324() | HPM | FULL | "DURETE EAU SORTIE ADOUC" | "PPM " | " " | "EA " | " " | EA | 01 | 3 | 9 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | 0.000000 | 60.00000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1.000000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | NOACTION | ENABLE
23995 | AI005324() | HPM | FULL | "OXYG DISSOUTSORTIE DEGAZ" | "PPB " | " " | "EA " | " " | EA | 01 | 3 | 9 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 8.200000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 8.000000 | LOW | CUTOUT | -1.00000 | -------- | -------- | -------- | NOACTION | DISABLE | NOACTION | CUTOUT | --------
24041 | AI006324() | HPM | FULL | "PH CONDENCE MACHINE 10 " | "pH " | " " | "EA " | " " | EA | 01 | 3 | 9 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 14.00000 | 0.000000 | D1 | 14.00000 | 0.000000 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 8.500000 | 25 | -- | NONE | NONE | 0 | 0 | HALF | 9.400000 | LOW | CUTOUT | 7.200000 | -------- | -------- | -------- | NOACTION | ENABLE | LOW | CUTOUT | --------
24087 | VIR830311() | HPM | FULL | "VIBRAT VENTIINDUIT NORD " | "PO/SEC " | " " | "LG " | " " | LG | 01 | 3 | 11 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 1.000000 | 0.000000 | D3 | 1.200000 | -0.20000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.100000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 0.300000 | LOW | CUTOUT | 0.000000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
24133 | VIR831311() | HPM | FULL | "VIBRAT VENTI INDUIT SUD " | "PO/SEC " | " " | "LG " | " " | LG | 01 | 3 | 11 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 1.000000 | 0.000000 | D3 | 1.200000 | -0.20000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 0.300000 | LOW | CUTOUT | -0.01000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
24179 | FI753C140() | HPM | FULL | "DEBIT EAU FRRETOUR P-550" | "L/MIN " | " " | "DE " | " " | DE | 01 | 3 | 9 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 20000.00 | 0.000000 | D0 | 25000.00 | -5000.00 | NOCLAMP | 0.000000 | 0.000000 | -- | ONLYAUTO | 10000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 20000.00 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | DISABLE
24264 | FI030364() | HPM | FULL | "EAU RECUPEREE MP#4 " | "L/M " | " " | " " | " " | LG | 01 | 3 | 6 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D1 | 2400.000 | -400.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE
24304 | FI028311() | HPM | FULL | "EAU CLARIFIEE VERS EPUR." | "L/M " | " " | " " | " " | LG | 01 | 3 | 6 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D1 | 2400.000 | -400.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- |  |  | -------- |  | -------- | -------- | LOW | ENABLE

## HPM3 ANOUTNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PNTMODTY | OPTDIR | OPCHAR | $OPTOL | OUTIND | $OLDEVDS | OPIN1 | OPOUT1 | OPIN2 | OPOUT2 | OPIN3 | OPOUT3 | OPIN4 | OPOUT4
17753 | PV002A364() | HPM | COMPONNT | "PRES. EAU MOULIN (VALVE)" | "% " | "VALVE " | " " | " " | DE | 01 | 3 | 12 | 1 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
17771 | PV311310() | HPM | COMPONNT | "PRESSION SOUFFLANTE " | "% " | " " | " " | " " | DV | 01 | 3 | 12 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17789 | I_P312A310() | HPM | COMPONNT | "PRESSION VAPEUR 800 KPA " | "% " | " " | " " | " " | DV | 01 | 3 | 12 | 4 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17807 | I_P312B310() | HPM | COMPONNT | "PRESSION VAPEUR 800 KPA " | "% " | " " | " " | " " | DV | 01 | 3 | 13 | 2 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17825 | I_P313A310() | HPM | COMPONNT | "PRESSION VAPEUR 210 KPA " | "% " | " " | " " | " " | DV | 01 | 3 | 12 | 5 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17843 | I_P313B310() | HPM | COMPONNT | "PRESSION VAPEUR 210 KPA " | "% " | " " | " " | " " | DV | 01 | 3 | 13 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17861 | LV001321() | HPM | COMPONNT | "NIVEAU RESERVOIR MAZOUT " | "% " | " " | " " | " " | MZ | 01 | 3 | 12 | 6 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17879 | PV060321() | HPM | COMPONNT | "PRES. MAZOUT CHAUDIERES " | "% " | " " | " " | " " | MZ | 01 | 3 | 12 | 7 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17897 | TV804321() | HPM | COMPONNT | "TEMP. MAZOUT CHAUDIERES " | "% " | " " | " " | " " | MZ | 01 | 3 | 12 | 8 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
17915 | I_P001A324() | HPM | COMPONNT | "NIVEAU RES. DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 12 | 9 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
17933 | I_P001B324() | HPM | COMPONNT | "NIVEAU RES. DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 13 | 4 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
17951 | I_P010A324() | HPM | COMPONNT | "NIVEAU RES. CONDENSE " | "% " | " " | " " | " " | EA | 01 | 3 | 12 | 10 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
17969 | I_P010B324() | HPM | COMPONNT | "NIVEAU RES. CONDENSE " | "% " | " " | " " | " " | EA | 01 | 3 | 13 | 5 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
17987 | LV011324() | HPM | COMPONNT | "NIV.RES.VIDANGE CONTINUE" | "% " | " " | " " | " " | EA | 01 | 3 | 12 | 11 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
18005 | I_P030A324() | HPM | COMPONNT | "PRESSION DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 12 | 13 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18023 | I_P030B324() | HPM | COMPONNT | "PRESSION DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 13 | 6 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18041 | SU080324() | HPM | COMPONNT | "DEBIT PHOSPHATE (POMPE) " | "% " | " " | " " | " " | EA | 01 | 3 | 20 | 1 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18059 | SU081324() | HPM | COMPONNT | "DEBIT SULPHITE (POMPE) " | "% " | " " | " " | " " | EA | 01 | 3 | 20 | 2 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18077 | SU082324() | HPM | COMPONNT | "DEBIT AMINE (POMPE) " | "% " | " " | " " | " " | EA | 01 | 3 | 20 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18119 | PV022324() | HPM | COMPONNT | "PRESSION EAU CHAUFFERIE " | "% " | " " | " " | " " | EA | 01 | 3 | 12 | 2 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
18137 | PV023324() | HPM | COMPONNT | "PRES.EAU ALIM.CHAUDIERES" | "% " | " " | " " | " " | EA | 01 | 3 | 12 | 12 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18155 | SU002B364() | HPM | COMPONNT | "PRES. EAU MOULIN (POMPE)" | "% " | "POMPE " | " " | " " | DE | 01 | 3 | 13 | 1 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
18739 | OP001311() | HPM | COMPONNT | "SORTIE DE LC001311 " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 16 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
20961 | LV001311() | HPM | COMPONNT | "NIVEAU CHAUDIERE #1" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 12 | 14 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
20979 | FZ004A_B311() | HPM | COMPONNT | "DEBIT AIR BRULEURS CH1" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 12 | 15 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
20997 | FV005311() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #1" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 12 | 16 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21015 | FV006311() | HPM | COMPONNT | "DEBIT HUILE CHAUDIERE #1" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 13 | 7 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21033 | SU009311() | HPM | COMPONNT | "VITESSE CONV. A VIS " | "% " | " " | "SE " | " " | SE | 01 | 3 | 13 | 8 | AO_16 | DIRECT | ON | 0.000000 | DIRECT | ENABLE | 16.50000 | -0.10000 | 16.55000 | 16.55000 | 25.00000 | 25.00000 | 100.0000 | 100.0000
21059 | SU922311() | HPM | COMPONNT | "VITESSE CONV.CENDRES" | "% " | " " | "LG " | " " | LG | 01 | 3 | 13 | 9 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21077 | SU012A_B311() | HPM | COMPONNT | "NIV. CHAMBRE DE CONTACT " | "% " | " " | "LG " | " " | LG | 01 | 3 | 20 | 5 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21095 | PV031311() | HPM | COMPONNT | "PRES. VAPEUR ATOMISANTE " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 6 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21113 | FZ040A_B311() | HPM | COMPONNT | "DEBIT AIR FORCE " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 7 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
21131 | PZ041A311() | HPM | COMPONNT | "PRESSION AIR FORCE " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 8 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
21149 | SU042311() | HPM | COMPONNT | "PRESSION FOYER " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 9 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21167 | PZ043311() | HPM | COMPONNT | "PRESSION AIR SUR GRILLE " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 10 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21225 | AV008311() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #1 " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 4 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21389 | FZ044311() | HPM | COMPONNT | "DEBIT AIR SUR GRILLE " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 14 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
21585 | PV499303() | HPM | COMPONNT | "AIR INST. EMBALLEUSE " | "% " | " " | " " | " " | AX | 01 | 3 | 20 | 12 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23270 | SU098311() | HPM | COMPONNT | "VITESSE GRILLE MOBIL" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 21 | 1 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23288 | SUYYY311() | HPM | COMPONNT | "VITESSE CONV. YYY " | "% " | " " | "SE " | " " | SE | 01 | 3 | 21 | 2 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23330 | SU093311() | HPM | COMPONNT | "VITESSE CONV. #224 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 13 | 10 | AO_16 | DIRECT | ON | 0.000000 | DIRECT | ENABLE | 25.00000 | 50.00000 | 50.00000 | 66.60000 | 75.00000 | 83.20000 | 100.0000 | 100.0000
23356 | SU094311() | HPM | COMPONNT | "VITESSE CONV. 231 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 21 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23374 | SU095311() | HPM | COMPONNT | "VITESSE CONV. 232 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 21 | 4 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23392 | SU096311() | HPM | COMPONNT | "VITESSE CONV. 233 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 21 | 5 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23410 | SU097311() | HPM | COMPONNT | "VITESSE CONV. 234 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 21 | 6 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23548 | I_P093311() | HPM | COMPONNT | "POSITION CHARRUE #2 " | "% " | " " | " " | " " | SE | 01 | 3 | 13 | 11 | AO_16 | REVERSE | OFF | 0.000000 | REVERSE | ENABLE
23769 | PV400311() | HPM | COMPONNT | "PRESSION AIRLAVEUR A GAZ" | "% " | " " | "LG " | " " | LG | 01 | 3 | 20 | 13 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
23851 | FZ450311() | HPM | COMPONNT | "DEBIT AIR DIST.ECORCES" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | 11 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE

## HPM3 ARRAY
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | EXTDATA | IOPNUM | FTANUM | DEVADDR | SCANPRI | AUXDATA1 | AB_DATA1 | AUXDATA2 | AB_DATA2 | AUXDATA3 | AB_DATA3 | AUXDATA4 | AB_DATA4 | FLSTIX | NFLAG | NNSTIX | NNUMERIC | STRSTIX | STRLEN | NSTRING | TIMESTIX | NTIME | SPLOCK | FLDESC | NNDESC | STRDESC | TIMEDESC | $ADD | STR16(001) | STR16(003) | STR16(005) | STR16(007) | STR16(009) | STR16(011) | STR16(013) | STR16(015) | STR16(017) | STR32(002) | STR32(003) | STR32(005) | STR32(006) | STR32(007) | STR32(008) | STR32(009) | STR32(011) | STR32(012) | STR32(013) | STR32(014) | STR32(015) | STR32(016) | STR32(017) | STR32(018) | STR32(019) | STR32(020) | STR32(021) | STR32(022) | STR32(023) | STR32(024) | STR32(025) | STR32(026) | STR32(027) | STR32(028) | STR32(029) | STR32(030) | STR8(001) | STR8(005) | STR8(008) | STR8(012) | STR8(015) | STR8(018) | STR8(021) | STR32(010) | STR32(001)
86 | FL_1_AXCH() | HPM | FULL | "COMM. 256 FLAG AXCH " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 4 | -- | "----------------" | IO_FL | 18 | 1 | 107.0 | LOW | -------- | -------- | 1.500000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 5745 | 256 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC AXCH MODBUS 256 BIT A PARTIR DE 360-16 A 375-16 " | " " | " " | " " | ON
127 | FL_1_ACH1() | HPM | FULL | "COMM. 368 FLAG ACH1 " | "MODBUS " | " " | " " | C1 | 01 | 3 | 0 | 1 | -- | "----------------" | IO_FL | 18 | 1 | 32.00 | HIGH | -------- | -------- | 1.500000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1.000 | 368 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ACH1 MODBUS 368 BIT A PARTIR DE 00001 A 00368 " | " " | " " | " " | ON
197 | NN_1_AXCH() | HPM | FULL | "COMM. 30 REGISTRE AXCH " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 5 | -- | "----------------" | IO_NN | 18 | 1 | 107.0 | LOW | -------- | -------- | 1.500000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 40700 | 30 | 0.000 | 8 | 0 | 0.00 | 0 | SUPERVIS | " " | "COMM.PLC AXCH MODBUS 30 REGISTRE A PARTIR DE 700 A 729 " | " " | " " | ON
238 | FL_1_ATB() | HPM | FULL | "COMM. 48 FLAG ATB " | "MODBUS " | " " | " " | EA | 01 | 3 | 0 | 9 | -- | "----------------" | IO_FL | 18 | 2 | 108.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 5745 | 48 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ATB MODBUS 48 BIT A PARTIR DE 360-16 A 362-16 " | " " | " " | " " | ON
279 | FL_1_SD() | HPM | FULL | "COMM. 48 FLAG SD " | "MODBUS " | " " | " " | EA | 01 | 3 | 0 | 8 | -- | "----------------" | IO_FL | 18 | 2 | 101.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 5745 | 48 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC SD MODBUS 48 BIT A PARTIR DE 360-16 A 362-16 " | " " | " " | " " | ON
320 | NN_1_ACH1() | HPM | FULL | "COMM. 20 REGISTRE ACH1 " | "MODBUS " | " " | " " | C1 | 01 | 3 | 0 | 2 | -- | "----------------" | IO_NN | 18 | 1 | 32.00 | LOW | -------- | -------- | 1.500000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 40626 | 20 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COMM.PLC ACH1 MODBUS 20 REGISTRE A PARTIR DE 40626 A 40645 " | " " | " " | ON
1967 | FL_1_FISCHER1() | HPM | FULL | "16 FLAG DU FFC008364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 12 | -- | "----------------" | IO_FL | 14 | 1 | 32.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1025 | 16 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COM. DE FFC008364 PAR MODBUS 16 BITS A PARTIR DE L1024 A L1040 " | " " | " " | " " | ON
2864 | BUT_PAGE_BAS() | HPM | FULL | " " | " " | " " | " " | AX | 01 | 3 | 0 | 21 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 51.00 | 16 | 25 | 0.00 | 0 | ENGINEER | " " | " " | "DISPLAY POUR BOUTON PAGE DU BAS " | " " | ON | "C1 " STR16(002)="NO_TEL " | "C4 " STR16(004)="C6 " | "C7GN " STR16(006)="C7MZ " | "SE " STR16(008)="C8 " | "CR " STR16(010)="INTEGRE " | "FQ " STR16(012)="MZ " | "LG " STR16(014)="EA " | "DE " STR16(016)="CE " | "DV " STR16(018)="AX "
3589 | TAG_PAGE_BAS() | HPM | FULL | " " | " " | " " | " " | AX | 01 | 3 | 0 | 20 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 1.000 | 16 | 25 | 0.00 | 0 | OPERATOR | " " | " " | "TAGNAME POUR LA PAGE DU BAS " | " " | ON | "FT003311 " STR16(002)="FI044316 " | "FT003317 " STR16(004)="TMA_HR_311 " | "FT003318 " STR16(006)="FI003314 " | "PC310310 " STR16(008)="PI499310 " | "LC008316 " STR16(010)="PC312310 " | "PI498310 " STR16(012)="PC023324 " | "PC313310 " STR16(014)="PC002B364 " | "LC001324 " STR16(025)="CVVBB "
3658 | NN_3_AXCH() | HPM | FULL | "COMM. 30 REGISTRE AXCH " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 7 | -- | "----------------" | IO_NN | 18 | 1 | 107.0 | LOW | -------- | -------- | 1.500000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 40760 | 30 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COMM.PLC AXCH MODBUS 30 REGISTRE A PARTIR DE 760 A 789 " | " " | " " | ON
3791 | FL_1_ASAE() | HPM | FULL | "COMM. 96 FLAG ASAE " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 10 | -- | "----------------" | IO_FL | 14 | 1 | 31.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1745 | 96 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ASAE MODBUS 96 BIT A PARTIR DE 1745 A 1840 " | " " | " " | " " | ON
4674 | NOM_EMPLOYE() | HPM | FULL | "ARRAY ASCII NOM EMPLOYE " | " " | " " | " " | AX | 01 | 3 | 0 | 24 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 101.0 | 32 | 40 | 0.00 | 0 | SUPERVIS | " " | " " | "ARRAY ASCII STRING(32) POUR LE NOM DES EMPLOYES " | " " | ON | [9 empty] | "BOISSONNEAULT, MARC(REPONDEUR) " | "BERGERON, ANDRE " | "CRETE, PIERRE-LOUIS " | "DELACHEVROTIERE, FRANCOIS " | "GERVAIS, ALAIN " | "FRAPPIER, MARTIN " | "LACOUTURE, RENE " | "LEBLANC, PATRICK " | "LEMAIRE, ALEXANDRE " | "LEMIRE, JONATHAN " | "PAQUET, ERIC " | "MONGRAIN, GUY " | "POLIQUIN, MICHEL " | "RACETTE, FRANCOIS " | ", " | "ROUETTE, SERGE " | "ROUSSEAU, STEPHANE " | "TURCOTTE, JEAN " | ", " | "DESHAIES ( DIESEL ) " | "BELANGER REFRIGERATION(URGENCE " | "BERGER, DANY (BELANGER REFRIGE " | ", " | "TRIO-JET " | "ACIDE PHOSPH A 85%(SYLVIE LANDRY" | "UREE GRANULAIRE (SYLVIE LANDRY)" | "SOUDE CAUSTIQUE (OLIN) "
11179 | NN_1_FISCHER1() | HPM | FULL | "16 NUM. DU FFC008364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 13 | -- | "----------------" | IO_NN | 14 | 1 | 32.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 90641 | 16 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COM. DE FFC008364 PAR MODBUS 16 BITS A PARTIR DE C640 A C656 " | " " | " " | ON
11220 | FL_1_FISCHER2() | HPM | FULL | "16 FLAG DU TI010364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 14 | -- | "----------------" | IO_FL | 14 | 1 | 33.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1025 | 16 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COM. DE TI010364 PAR MODBUS 16 BITS A PARTIR DE L1024 A L1040 " | " " | " " | " " | ON
11261 | NN_1_FISCHER2() | HPM | FULL | "16 NUM. DU TI010364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 15 | -- | "----------------" | IO_NN | 14 | 1 | 33.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 90641 | 16 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COM. DE TI010364 PAR MODBUS 16 BITS A PARTIR DE C640 A C656 " | " " | " " | ON
11302 | FL_1_FISCHER3() | HPM | FULL | "16 FLAG DU FFC009364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 16 | -- | "----------------" | IO_FL | 14 | 1 | 34.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1025 | 16 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COM. DE FFC009364 PAR MODBUS 16 BITS A PARTIR DE L1024 A L1040 " | " " | " " | " " | ON
11343 | NN_1_FISCHER3() | HPM | FULL | "16 NUM. DU FFC009364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 17 | -- | "----------------" | IO_NN | 14 | 1 | 34.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 90641 | 16 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COM. DE FFC009364 PAR MODBUS 16 BITS A PARTIR DE C640 A C656 " | " " | " " | ON
11384 | FL_1_FISCHER4() | HPM | FULL | "16 FLAG DU FFC014364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 18 | -- | "----------------" | IO_FL | 14 | 1 | 35.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1025 | 16 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COM. DE FFC014364 PAR MODBUS 16 BITS A PARTIR DE L1024 A L1040 " | " " | " " | " " | ON
11425 | FL_1_FISCHER5() | HPM | FULL | "16 FLAG DU LC004364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 22 | -- | "----------------" | IO_FL | 14 | 1 | 36.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 1025 | 16 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COM. DE LC004364 PAR MODBUS 16 BITS A PARTIR DE L1024 A L1040 " | " " | " " | " " | ON
11466 | NN_1_FISCHER4() | HPM | FULL | "16 NUM. DU FFC014364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 19 | -- | "----------------" | IO_NN | 14 | 1 | 35.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 90641 | 16 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COM. DE FFC014364 PAR MODBUS 16 BITS A PARTIR DE C640 A C656 " | " " | " " | ON
11507 | NN_1_FISCHER5() | HPM | FULL | "16 NUM. DU LC004364 " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 23 | -- | "----------------" | IO_NN | 14 | 1 | 36.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 90641 | 16 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COM. DE LC004364 PAR MODBUS 16 BITS A PARTIR DE C640 A C656 " | " " | " " | ON
12654 | NO_EMPLOYE() | HPM | FULL | "ARRAY ASCII NO. EMPLOYE " | " " | " " | " " | AX | 01 | 3 | 0 | 25 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 261.0 | 8 | 40 | 0.00 | 0 | SUPERVIS | " " | " " | "ARRAY ASCII STRING(32) POUR LE NUMERO DES EMPLOYES " | " " | ON | [36 empty] | ". " STR8(002)="2117 " STR8(003)="2671 " | "2583 " STR8(006)="6481 " STR8(007)="6089 " | "2700 " STR8(009)="1004 " STR8(011)="2699 " | "2701 " STR8(013)="2434 " STR8(014)="2574 " | "2760 " STR8(016)="2121 " STR8(017)="6533 " | ", " STR8(019)="838 " STR8(020)="2481 " | "017 "
12690 | NOM_PAGETTE() | HPM | FULL | "ARRAY ASCII NOM PAGETTE " | " " | " " | " " | AX | 01 | 3 | 0 | 27 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 461.0 | 32 | 40 | 0.00 | 0 | SUPERVIS | " " | " " | "ARRAY ASCII STRING(32) POUR LE NOM DE LA PAGETTE " | " " | ON | [10 empty] | "ELECTRIQUE RELEVE " |  | "MECANICIEN DE NUIT " | "MECANICIEN DE RELEVE (JOUR/SOIR " | "TUYAUTEUR DE RELEVE " | "HYDRAULIQUE " | "PERRON, ALEX " |  |  | "CONTREMAITRE MP#7-10 " |  | "CONTENEURS A DECHETS (VIDER) " | "CLARIFICATEUR " | "TANGUAY, FRANCINE " | "INFIRMERIE " | "LABORATOIRE CHAUFFERIE " | "BELANGER , GEORGES " | "RESERVOIR A MAZOUT " | "TMP " | "TMP CONTREMAITRE " | "TRAITEMENT EAUX USEES " | "PIZZERIA BRAVO " | "INFORMATIQUE " |  | "NALCO ( BENOIT ) " | [8 empty] | "HYDRAULIQUE - CONTREMAITRE "
12740 | NO_PAGETTE() | HPM | FULL | "ARRAY ASCII NO.PAGETTE " | " " | " " | " " | AX | 01 | 3 | 0 | 28 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 621.0 | 32 | 40 | 0.00 | 0 | SUPERVIS | " " | " " | "ARRAY ASCII STRING(32) POUR LE NUMERO DE LA PAGETTE " | " " | ON | [10 empty] | "#1515 " |  | "#1528 " | "#1673 " | "#1674 " | "#4414; PAGE#1524 " | "#4483 " |  |  | "#4743; PAGE # 1526 " |  | "4292 " | "#4220 " | "514-247-8152 " | "#4213 " | "#4365 " | "#4217 " | "#4406 " | "#4336 " | "#4341 (PAGE: 1557) " | "#4264 PAGE 1527 OU 695-1891 " | "819-379-1272 " | "#4759 " | ", " | ", " | [8 empty] | "#4338 "
12791 | TEL_EMPLOYE() | HPM | FULL | "ARRAY ASCII TEL EMPLOYE " | " " | " " | " " | AX | 01 | 3 | 0 | 26 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 301.0 | 32 | 40 | 0.00 | 0 | SUPERVIS | " " | " " | "ARRAY ASCII STRING(32) POUR LE NUMERO DE TELEPHONE DE L'EMPLOYE " | " " | ON | [9 empty] | "694-1170 " | "(819) 539-6031 (CELL: 531-9208) " | "CELL:698-0901 " | "840-7649 (CELL 371-4541) " | "373-4843 ( CELL: 609-2597 ) " | "819-228-1223 CELL 819-668-9814 " | "233-4275 (CELL: 244-5025) " | "819-374-5229, CELL 819-696-7301 " | "819-841-0151 CELL 418-717-0077 " | "819-406-2122 CELL 384-9696 " | "(819) 840-2561 " | "819-731-3717, CELL 819-534- 6277" | "294-1571 " | "( CELL: 609-9882) " | ", " | "379-6758 " | "909-6012 " | "691-2715 " |  | "BUR.:222-5623; URG.:373-5504 " | "819-697-1110 EXT 206 " | "CELL: 819-384-9953 " | ". " | "819-696-5267 " | "1-800-361-0284 EX 226 BRENNTAG " | "1-800-361-0284 EX 226 BRENNTAG " | "819-294-1203 " | [8 empty] | ". "
16049 | NN_1_ASAE() | HPM | FULL | "COMM. 2 NUMERIC ASAE " | "MODBUS " | " " | " " | AX | 01 | 3 | 0 | 11 | -- | " " | IO_NN | 14 | 1 | 31.00 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 30003 | 2 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COMMUNICATION POINT NUMERIC AVEC PLC ASAE DEBUTANT A 40003 " | " " | " " | ON

## HPM3 DIINNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | PNTMODTY | DITYPE | STATETXT(1) | STATETXT(0) | BOXCLR(1) | BOXCLR(0) | INPTDIR | PVSRCOPT | $AUXUNIT | $REALARM | ALMOPT | PVNORMAL | $DLYOPT | DLYTIME | OFFNRMPR | $OFSELCT | ALENBST | EVTOPT
18453 | PDSH048311() | HPM | FULL | "PRES.DIFF.SEPARATEUR HI " | " " | " " | "LG " | " " | LG | 01 | 3 | 17 | 8 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
18484 | YT517A311() | HPM | FULL | "BRULEUR NORD ARRETE " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 17 | 6 | -- | DI | STATUS | "ON " | "OFF " | YELLOW | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | OFF | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
18543 | YT517B311() | HPM | FULL | "BRULEUR SUD ARRETE " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 17 | 7 | -- | DI | STATUS | "ON " | "OFF " | YELLOW | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | OFF | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
18574 | PSLL400311() | HPM | FULL | "DEBIT AIR GICLEURS LL " | " " | " " | "LG " | " " | LG | 01 | 3 | 17 | 9 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
18884 | LE010321() | HPM | FULL | "SONDE LSH010321 " | " " | " " | " " | " " | MZ | 01 | 3 | 17 | 1 | -- | DI | STATUS | "NORMAL " | "FAUTE " | GREEN | RED | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
18915 | LSH010321() | HPM | FULL | "HAUT NIV.RES.MAZOUT INT." | " " | " " | " " | " " | MZ | 01 | 3 | 17 | 2 | -- | DI | STATUS | "NORMAL " | "HAUT " | GREEN | RED | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
18946 | LE011321() | HPM | FULL | "SONDE LSHH011321 " | " " | " " | " " | " " | MZ | 01 | 3 | 17 | 3 | -- | DI | STATUS | "NORMAL " | "FAUTE " | GREEN | RED | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
19605 | VC005311() | HPM | FULL | "TRACKING CONDIT. BAS FEU" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 17 | 11 | -- | DI | STATUS | "ON " | "OFF " | YELLOW | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | OFF | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
21283 | HS005_006311() | HPM | COMPONNT | "SELECTEUR GAZ / HUILE " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 17 | 4 |  | DI | STATUS
21447 | FSL021311() | HPM | FULL | "DEBIT EAU GICLEURS " | " " | " " | "LG " | " " | LG | 01 | 3 | 17 | 5 | -- | DI | STATUS | "ALARME " | "NORMAL " | YELLOW | GREEN | REVERSE | ONLYAUTO | -- |  | NONE | [6 empty] | NONE
21603 | ASHH080321() | HPM | FULL | "ALARME VAPEUR HUILE" | " " | " " | "MZ " | " " | MZ | 01 | 3 | 17 | 12 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | LOW | CUTOUT | ENABLE | NONE
21634 | VC043311() | HPM | FULL | "TRACKING DE LSLL011311 " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 17 | 10 | -- | DI | STATUS | "NORMAL " | "TRACK " | GREEN | RED | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE

## HPM3 FLAGNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | STATETXT(1) | STATETXT(0) | PV | BOXCLR(1) | BOXCLR(0) | $AUXUNIT | $REALARM | OFFNRMPR | $OFSELCT | ALENBST | EIPPCODE
63 | YT090311() | HPM | FULL | "BRULEUR #2 EN ARRET " | " " | " " | "BRC1 " | " " | C1 | 01 | 3 | 67 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
361 | FSL004311() | HPM | FULL | "BAS DEBIT AIR COMBUSTION" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 68 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
384 | A6_B9_364() | HPM | FULL | "POMPE EAU FRAICHE #60 " | "6-B9 " | "POMPE#60" | " " | " " | DE | 01 | 3 | 1 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
566 | PSL499311() | HPM | FULL | "BASSE PRES. AIR INSTRUME" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 69 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
589 | A22_5N_311() | HPM | FULL | "CONVOYEUR A CENDRE " | "22-5N " | "CON.CEND" | " " | " " | LG | 01 | 3 | 102 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
612 | YT22_5N_311() | HPM | FULL | "FAUTE ONDULEUR CONV.CEND" | " " | "FT.ONDUL" | " " | " " | LG | 01 | 3 | 103 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
635 | A26_5N_311() | HPM | FULL | "P.HYD.POUSSOIR A CENDRE " | "26-5N " | "P.HYD.PO" | " " | " " | LG | 01 | 3 | 101 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1551 | A2_D4_364() | HPM | FULL | "POMPE EAU FRAICHE #308 " | "2-D4 " | "POMP#308" | " " | " " | DE | 01 | 3 | 2 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
1574 | YT2_D4_364() | HPM | FULL | "FAUTE OUNDULEUR POMP#308" | " " | "POMP#308" | " " | " " | DE | 01 | 3 | 3 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
1597 | A26_V1_364() | HPM | FULL | "POMPE EAU FRAICHE #324 " | "26-V1 " | "POMP#324" | " " | " " | DE | 01 | 3 | 4 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
1620 | A5_D1_364() | HPM | FULL | "DEPART POMPE #550 " | "5-D1 " | "POMP#550" | " " | " " | DE | 01 | 3 | 5 | -- | "ALARME " | "NORMAL " | ALARME | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
1817 | A5_5A_324() | HPM | FULL | "POMPE RECIRCULAT. ADOU. " | "5-5A " | "P.REC.AD" | " " | " " | EA | 01 | 3 | 6 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1840 | A12_5A_324() | HPM | FULL | "POMPE SAUMURE ADOU. " | "12-5A " | "P.SAU.AD" | " " | " " | EA | 01 | 3 | 7 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1944 | A1_B9_364() | HPM | FULL | "POMPE EAU FRAICHE #116 " | "1-B9 " | "POMP#116" | " " | " " | DE | 01 | 3 | 10 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
2177 | A2_B9_364() | HPM | FULL | "POMPE EAU FRAICHE #115 " | "2-B9 " | "POMP#115" | " " | " " | DE | 01 | 3 | 11 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
2200 | LSH240324() | HPM | FULL | "HAUT NIV.BAC A SAUMURE " | " " | "BAC SAUM" | " " | " " | EA | 01 | 3 | 8 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2223 | LSL240324() | HPM | FULL | "BAS NIV.BAC A SAUMURE " | " " | "BAC SAUM" | " " | " " | EA | 01 | 3 | 9 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3095 | A1_5N_311() | HPM | FULL | "VENTILATEUR INDUIT " | " " | " " | "LG " | " " | C1 | 01 | 3 | 15 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3118 | A30_M4_311() | HPM | FULL | "VENTI.LAVEUR DE GAZ " | " " | " " | "LG " | " " | LG | 01 | 3 | 16 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3141 | A6_5A_311() | HPM | FULL | "COMPRESSEUR #9 " | " " | " " | "LG " | " " | LG | 01 | 3 | 18 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3164 | A8_T2_311() | HPM | FULL | "VENTIL. AIR SECONDAIRE " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 19 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3530 | A1_W5_324() | HPM | FULL | "POMPE ALIM.CHAUDIERE #1 " | "1-W5 " | "POMPE #1" | " " | " " | EA | 01 | 3 | 12 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3553 | A7_T2_324() | HPM | FULL | "POMPE ALIM.CHAUDIERE #3 " | "7-T2 " | "POMPE #3" | " " | " " | EA | 01 | 3 | 13 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3699 | SSL096311() | HPM | FULL | "VIT.NULLE CONVOYEUR 233 " | " " | " " | "SE " | " " | SE | 01 | 3 | 96 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3722 | SSL097311() | HPM | FULL | "VIT.NULLE CONVOYEUR 234 " | " " | " " | "SE " | " " | SE | 01 | 3 | 97 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3745 | LSH111B311() | HPM | FULL | "HAUT NIVEAU CHUTE CV.231" | " " | " " | "SE " | " " | SE | 01 | 3 | 125 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3768 | LSH112B311() | HPM | FULL | "HAUT NIVEAU CHUTE CV.232" | " " | " " | "SE " | " " | SE | 01 | 3 | 126 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3832 | YT001364() | HPM | FULL | "FAUTE DRIVE RIVER PUMP#3" | " " | " " | "CE " | " " | CE | 01 | 3 | 70 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3855 | YT002364() | HPM | FULL | "FAUTE DRIVE RIVER PUMP#4" | " " | " " | "CE " | " " | CE | 01 | 3 | 71 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3878 | A9_URG0_364() | HPM | FULL | "ARRET POMPE DU FLEUVE #2" | " " | " " | "CE " | " " | CE | 01 | 3 | 72 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3901 | A7_6A_364() | HPM | FULL | "ARRET POMPE DU FLEUVE #3" | " " | " " | "CE " | " " | CE | 01 | 3 | 73 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3924 | A2_K2_364() | HPM | FULL | "ARRET POMPE DU FLEUVE #4" | " " | " " | "CE " | " " | CE | 01 | 3 | 74 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
4570 | PSL048311() | HPM | FULL | "BASSE PRES. AIR INDUIT" | " " | " " | "LG " | " " | LG | 01 | 3 | 123 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6579 | LSH010311() | HPM | FULL | "HAUT NIVEAU HYDRASTEP C1" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 20 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6602 | LSH011311() | HPM | FULL | "HAUT NIV. COLONNE EAU C1" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 21 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6625 | A5_5N_311() | HPM | FULL | "VENTILATEUR TIRAGE FORCE" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 17 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6648 | LSH015311() | HPM | FULL | "H.NIVEAU.CHUTE CONV.VIS " | " " | " " | "SE " | " " | SE | 01 | 3 | 22 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6671 | LSH016311() | HPM | FULL | "H.NIVEAU.CHUTE CONV.100B" | " " | " " | "SE " | " " | SE | 01 | 3 | 23 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6694 | LSH017311() | HPM | FULL | "HAUT NIVEAU TREMIE " | " " | " " | "SE " | " " | SE | 01 | 3 | 24 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6717 | LSHH010311() | HPM | FULL | "T.HAUT NIV. HYDRASTEP C1" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 25 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
6740 | LSL010311() | HPM | FULL | "BAS NIVEAU HYDRASTEP C1 " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 26 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6763 | LSL011311() | HPM | FULL | "BAS NIV. COLONNE EAU C1 " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 27 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6786 | LSL018311() | HPM | FULL | "BAS NIV.UNITE.HYD.1 SILO" | " " | " " | "SE " | " " | SE | 01 | 3 | 28 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6809 | LSL019311() | HPM | FULL | "BAS NIV.UNITE.HYD.2 SILO" | " " | " " | "SE " | " " | SE | 01 | 3 | 29 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6832 | LSLL010311() | HPM | FULL | "T.BAS NIV. HYDRASTEP C1 " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 30 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
6855 | LSLL011311() | HPM | FULL | "T.BAS NIV.COLONNE EAU C1" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 31 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
6878 | PSH032311() | HPM | FULL | "HAUTE PRES.BALLON CH#1 " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 32 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6901 | PSH058311() | HPM | FULL | "H.PRES.GAZ PRINCIPALE C1" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 33 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6924 | PSH059311() | HPM | FULL | "H.PRESSION GAZ BRULEUR#2" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 34 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6947 | PSH042311() | HPM | FULL | "HAUTE PRESSION FOYER " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 122 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6970 | SSL042311() | HPM | FULL | "VIT.NUL MOT.VENT.INDUIT " | " " | " " | "LG " | " " | LG | 01 | 3 | 121 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
6993 | PSH068311() | HPM | FULL | "H.PRES.HYD.GRILLE MOBILE" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 37 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7016 | PSH504311() | HPM | FULL | "H.PRES.PILOTE GAZ CH#1 " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 38 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7039 | SSL102311() | HPM | FULL | "VITESSE GRILLE MOBILE " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 39 | -- | "ALARME " | "NORMAL " | ALARME | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7062 | PSHH032311() | HPM | FULL | "T.HAUTE PRES.BALLON CH#1" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 43 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
7085 | PSHH902311() | HPM | FULL | "T.H.PRESSION CHARGEUR #1" | " " | " " | "SE " | " " | SE | 01 | 3 | 44 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7108 | PSHH903311() | HPM | FULL | "T.H.PRESSION CHARGEUR #2" | " " | " " | "SE " | " " | SE | 01 | 3 | 45 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7131 | PSHH904311() | HPM | FULL | "T.H.PRESSION CHARGEUR #3" | " " | " " | "SE " | " " | SE | 01 | 3 | 46 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7154 | PSHH905311() | HPM | FULL | "T.H.PRESSION CHARGEUR #4" | " " | " " | "SE " | " " | SE | 01 | 3 | 47 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7177 | PSL022311() | HPM | FULL | "B.PRESSION EAU DOUCHE LG" | " " | " " | "LG " | " " | LG | 01 | 3 | 48 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7200 | PSL023311() | HPM | FULL | "B.PRES.EAU COMPRESSEUR#9" | " " | " " | "LG " | " " | LG | 01 | 3 | 49 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7223 | PSL052311() | HPM | FULL | "B.PRES.GAZ PRICIPALE C#1" | " " | " " | "BRC1 " | " " | C1 | 01 | 3 | 50 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7246 | PSL060311() | HPM | FULL | "B.PRES.HUILE BRULEURS C1" | " " | " " | "BRC1 " | " " | C1 | 01 | 3 | 51 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7269 | PSL067311() | HPM | FULL | "B.P.HUILE COMPRESSEUR #9" | " " | " " | "LG " | " " | LG | 01 | 3 | 52 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7292 | PSL400311() | HPM | FULL | "TRANSF.AIR INST.DEPOUSS." | " " | " " | "LG " | " " | LG | 01 | 3 | 53 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7315 | PSL504311() | HPM | FULL | "BAS PRES.PILOTE GAZ CH#1" | " " | " " | "BRC1 " | " " | C1 | 01 | 3 | 54 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7338 | SSL901311() | HPM | FULL | "VIT.NULLE ROUL.PIQUEUR " | " " | " " | "SE " | " " | SE | 01 | 3 | 55 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7361 | SSL923311() | HPM | FULL | "VIT.NULLE CONVOY.100-B " | " " | " " | "SE " | " " | SE | 01 | 3 | 57 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7384 | SSL924311() | HPM | FULL | "VIT.NULLE CONVOYEUR #224" | " " | " " | "SE " | " " | SE | 01 | 3 | 58 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7407 | TSH821311() | HPM | FULL | "H.TEMP.AIR COMPRESSEUR 9" | " " | " " | "LG " | " " | LG | 01 | 3 | 59 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7430 | TSHH819311() | HPM | FULL | "T.H.TEMP.UNITE HYD #1 " | " " | " " | "SE " | " " | SE | 01 | 3 | 60 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7453 | TSHH820311() | HPM | FULL | "T.H.TEMP.UNITE HYD #2 " | " " | " " | "SE " | " " | SE | 01 | 3 | 61 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7476 | TSL804311() | HPM | FULL | "B.TEMP.HUILE BRULEURS C1" | " " | " " | "BRC1 " | " " | C1 | 01 | 3 | 62 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7499 | URG_C224() | HPM | FULL | "ARRET URGENCE CONV.#224 " | " " | " " | "SE " | " " | SE | 01 | 3 | 63 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7522 | URG_SILO() | HPM | FULL | "ARRET URG.PANNEAU SILO " | " " | " " | "SE " | " " | SE | 01 | 3 | 64 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7545 | YT31_5N_311() | HPM | FULL | "DEF.VARIATEUR P.CENDRE#1" | " " | " " | "LG " | " " | LG | 01 | 3 | 65 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7568 | YT32_5N_311() | HPM | FULL | "DEF.VARIATEUR P.CENDRE#2" | " " | " " | "LG " | " " | LG | 01 | 3 | 66 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
7696 | LLL004364() | HPM | FULL | "TRES BAS NIV. CLARIFICA." | " " | " " | "CE " | " " | CE | 01 | 3 | 75 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
7719 | PSHH900311() | HPM | FULL | "T.H.PRES.HYD.CONVOY.VIS " | " " | " " | "SE " | " " | SE | 01 | 3 | 41 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
7822 | LLL005364() | HPM | FULL | "TRES BAS NIV.EAU CLAIRE " | " " | " " | "CE " | " " | CE | 01 | 3 | 76 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
9503 | A10_1A_4_364() | HPM | FULL | "AGITATEUR CLARIFICA. " | " " | " " | "CE " | " " | CE | 01 | 3 | 77 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
9654 | A10_1A_5_364() | HPM | FULL | "RATEAU CLARIFICA. " | " " | " " | "CE " | " " | CE | 01 | 3 | 78 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
9677 | A7_1A_3_364() | HPM | FULL | "VENTIL. FUITE BIOCIDE " | " " | " " | "CE " | " " | CE | 01 | 3 | 79 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
9796 | A7_1A_7_364() | HPM | FULL | "POMPES ALUN #2 #3 CLARI." | " " | " " | "CE " | " " | CE | 01 | 3 | 81 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
9819 | WSH068364() | HPM | FULL | "TIGE RATEAU CLARIFICA. " | " " | " " | "CE " | " " | CE | 01 | 3 | 80 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
9842 | A3_6A_3_364() | HPM | FULL | "TAMIS NORD " | " " | " " | "CE " | " " | CE | 01 | 3 | 82 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
9865 | A3_6A_2_364() | HPM | FULL | "TAMIS SUD " | " " | " " | "CE " | " " | CE | 01 | 3 | 83 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
10286 | A4_URGO_D17_364() | HPM | FULL | "GENARATRICE EN PANNE " | " " | " " | "CE " | " " | CE | 01 | 3 | 86 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
10379 | A5_1A_1_364() | HPM | FULL | "PUISARD CLARIFICA. " | " " | "POMPE " | "CE " | " " | CE | 01 | 3 | 85 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
10430 | PSL499364() | HPM | FULL | "BASSE PRES. AIR INSTR. " | " " | " " | "CE " | " " | CE | 01 | 3 | 84 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
10622 | YT18_B4_103() | HPM | FULL | "DEF.VARIATEUR CONV.#2 " | " " | " " | "COUR " | " " | AX | 01 | 3 | 87 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
11156 | SSL19_B4_103() | HPM | FULL | "INTERUP.VIT.CONV.CAOUT#1" | " " | " " | "COUR " | " " | AX | 01 | 3 | 88 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
11548 | YT001311() | HPM | FULL | "CONTOURNE PROTEC.COL.EAU" | " " | "PROTECT." | "C1 " | " " | C1 | 01 | 3 | 14 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
11571 | A2_4B_324() | HPM | FULL | "POMPES RES. COND. #636 " | " " | " " | "EA " | " " | EA | 01 | 3 | 89 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
11594 | A5_5B_324() | HPM | FULL | "POMPES RES. COND. #418 " | " " | " " | "EA " | " " | EA | 01 | 3 | 90 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
11707 | F4_URGO_D17() | HPM | FULL | "FEEDBACK GENERATRICE " | " " | "GENERAT." | "CE " | " " | CE | 01 | 3 | 91 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
12608 | PDSH251324() | HPM | FULL | "H.PRES.DIFF.FILTRE SUD " | " " | " " | "FAS " | " " | EA | 01 | 3 | 92 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
12631 | PDSH261324() | HPM | FULL | "H.PRES.DIFF.FILTRE NORD " | " " | " " | "FAN " | " " | EA | 01 | 3 | 93 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
12847 | LSH101311() | HPM | FULL | "H.NIVEAU.CONVOY.CENDRES " | " " | " " | "LG " | " " | LG | 01 | 3 | 42 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13017 | LSH050109() | HPM | FULL | "HAUT NIVEAU CHUTE 100A-B" | " " | " " | "SE1 " | " " | AX | 01 | 3 | 56 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13233 | SSL094311() | HPM | FULL | "VIT.NULLE CONVOYEUR 231 " | " " | " " | "SE " | " " | SE | 01 | 3 | 94 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13256 | SSL095311() | HPM | FULL | "VIT.NULLE CONVOYEUR 232 " | " " | " " | "SE " | " " | SE | 01 | 3 | 95 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13438 | YT41_5N_311() | HPM | FULL | "FAUTE VARIATEUR 41_5N " | " " | " " | "C1 " | " " | C1 | 01 | 3 | 113 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13461 | A41_5N_311() | HPM | FULL | "GRILLE MOBILE " | "41-5N " | "GRILLE " | "C1 " | " " | C1 | 01 | 3 | 104 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13484 | PDSH026311() | HPM | FULL | "H.PRES.DIFF.FILT.EAU REC" | " " | " " | "LG " | " " | LG | 01 | 3 | 35 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13507 | YS926311() | HPM | FULL | "FAUTE SYST. LUB.CH.SILO " | " " | " " | "SE " | " " | SE | 01 | 3 | 36 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13530 | LSH111A311() | HPM | FULL | "HAUT NIVEAU CONV. 231 " | " " | " " | "SE " | " " | SE | 01 | 3 | 98 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13553 | SSL925311() | HPM | FULL | "VIT.NULLE VENT. CHUTES " | " " | " " | "SE " | " " | SE | 01 | 3 | 100 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13657 | LSH112A311() | HPM | FULL | "HAUT NIVEAU CONV. 232 " | " " | " " | "SE " | " " | SE | 01 | 3 | 99 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13680 | LSH113A311() | HPM | FULL | "HAUT NIVEAU CONV. 233 " | " " | " " | "SE " | " " | SE | 01 | 3 | 105 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13703 | A43_5N_311() | HPM | FULL | "CONVOYEUR ECORCES 231 " | "43-5N " | "CON.ECOR" | " " | " " | SE | 01 | 3 | 106 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13726 | A44_5N_311() | HPM | FULL | "CONVOYEUR ECORCES 232 " | "44-5N " | "CON.ECOR" | " " | " " | SE | 01 | 3 | 107 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13749 | A45_5N_311() | HPM | FULL | "CONVOYEUR ECORCES 233 " | "45-5N " | "CON.ECOR" | " " | " " | SE | 01 | 3 | 108 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13772 | A46_5N_311() | HPM | FULL | "CONVOYEUR ECORCES 234 " | "46-5N " | "CON.ECOR" | " " | " " | SE | 01 | 3 | 109 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13795 | A48_5N_311() | HPM | FULL | "VENT. ENTREE ECORCES " | "48-5N " | "VENTILAT" | " " | " " | SE | 01 | 3 | 110 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13818 | A49_5N_311() | HPM | FULL | "DIFFUSEUR CHUTES ECORCES" | "49-5N " | "VENTILAT" | " " | " " | SE | 01 | 3 | 111 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13841 | APSL_089_311() | HPM | FULL | "AIR CAMERA VISUL. CH #1 " | " " | "AIR CAME" | " " | " " | SE | 01 | 3 | 112 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
13864 | LSH114A311() | HPM | FULL | "HAUT NIVEAU CONV. 234 " | " " | " " | "SE " | " " | SE | 01 | 3 | 114 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13887 | LSH113B311() | HPM | FULL | "HAUT NIVEAU CHUTE CV.233" | " " | " " | "SE " | " " | SE | 01 | 3 | 127 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13910 | YT43_5N_311() | HPM | FULL | "FAUTE VARIATEUR 43_5N " | " " | " " | "SE " | " " | SE | 01 | 3 | 115 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13933 | YT44_5N_311() | HPM | FULL | "FAUTE VARIATEUR 44_5N " | " " | " " | "SE " | " " | SE | 01 | 3 | 116 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13956 | YT45_5N_311() | HPM | FULL | "FAUTE VARIATEUR 45_5N " | " " | " " | "SE " | " " | SE | 01 | 3 | 117 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
13979 | YT46_5N_311() | HPM | FULL | "FAUTE VARIATEUR 46_5N " | " " | " " | "SE " | " " | SE | 01 | 3 | 118 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
14002 | YT47_5N_311() | HPM | FULL | "FAUTE VARIATEUR 47_5N " | " " | " " | "SE " | " " | SE | 01 | 3 | 119 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
14111 | PSL031311() | HPM | FULL | "BASSE PRES.VAPEUR ATOMIS" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 124 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
14164 | PSL041A311() | HPM | FULL | "BASSE PRESSION AIR FORCE" | " " | " " | "C1 " | " " | C1 | 01 | 3 | 120 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
14187 | LSH114B311() | HPM | FULL | "HAUT NIVEAU CHUTE CV.234" | " " | " " | "SE " | " " | SE | 01 | 3 | 128 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
15504 | YT083311() | HPM | FULL | "ALARME HAUTE OPACITE CH1" | " " | " " | "LG " | " " | LG | 01 | 3 | 129 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
15527 | YT080310() | HPM | FULL | "VALEUR HORS NORM.CH1,7,8" | " " | " " | "DV " | " " | DV | 01 | 3 | 130 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | DISABLE | --
15821 | YT027364() | HPM | COMPONNT | "1/6 PMP ALIM.EAU FRAICHE" | "OFF/ON " | "ALIM.EAU" | "DE " | " " | DE | 01 | 3 | 131 |  |  |  | ARRET
15911 | YT320364() | HPM | FULL | "FAUTE ASS.AIR SALLE ALUN" | "FAUTE " | "AIR ALUN" | "CE " | " " | CE | 01 | 3 | 132 | -- | "FAUTE " | "NORMAL " | FAUTE | RED | GREEN | -- | 0 | LOW | CUTOUT | DISABLE | --
15934 | HS100364() | HPM | FULL | "VALVE REMPLIS.RES. BUSAN" | "OUV/FERM" | "R-BUSAN " | "CE " | " " | CE | 01 | 3 | 133 | -- | "FERMER " | "OUVERT " | OUVERT | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
15957 | HS200364() | HPM | FULL | "VALVE REMPLIS.RES. NACLO" | "OUV/FERM" | "NACLO " | "CE " | " " | CE | 01 | 3 | 134 | -- | "FERMER " | "OUVERT " | OUVERT | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
15980 | YT310364() | HPM | FULL | "ALM GEN. PREP. BIOCIDE " | "ALARME " | "BIOCIDE " | "CE " | " " | CE | 01 | 3 | 135 | -- | "ALARME " | "NORMAL " | ALARME | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
16003 | LSH104364() | HPM | FULL | "FUITE PAROI RES. BUSAN " | "ALARME " | "FUITE " | "CE " | " " | CE | 01 | 3 | 136 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
16026 | LSH204364() | HPM | FULL | "FUITE PAROI RES. NACLO " | "ALARME " | "FUITE " | "CE " | " " | CE | 01 | 3 | 137 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
16178 | AS016E364() | HPM | COMPONNT | "FAUT DETECTEUR BIOCIDE " | "ALARME " | "FAUTE " | "CE " | " " | CE | 01 | 3 | 138 |  |  |  | NORMAL

## HPM3 LOGICNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | USERID | LOGMIX | LISRC(1) | LISRC(2) | LISRC(3) | LISRC(4) | LISRC(5) | LISRC(6) | LISRC(7) | LISRC(8) | LISRC(9) | LISRC(10) | LISRC(11) | LISRC(12) | LIBADOPT | LOSRC(1) | LODSTN(1) | LOENBL(1) | LOSRC(2) | LODSTN(2) | LOENBL(2) | LOSRC(3) | LODSTN(3) | LOENBL(3) | LOSRC(4) | LODSTN(4) | LOENBL(4) | LOSRC(5) | LODSTN(5) | LOENBL(5) | LOSRC(6) | LODSTN(6) | LOENBL(6) | LOSRC(7) | LODSTN(7) | LOENBL(7) | LOSRC(8) | LODSTN(8) | LOENBL(8) | LOSRC(9) | LODSTN(9) | LOENBL(9) | LOSRC(10) | LODSTN(10) | LOENBL(10) | LOSRC(11) | LODSTN(11) | LOENBL(11) | LOSRC(12) | LODSTN(12) | LOENBL(12) | NODESC | $AUXUNIT | $REALARM | ALENBST | C1PR | C1DESC | C1SRC | C2PR | C2DESC | C2SRC | C3PR | C3DESC | C3SRC | C4PR | C4DESC | C4SRC | EIPPCODE | LOGALGID(1) | LOGALGID(2) | LOGALGID(3) | LOGALGID(4) | LOGALGID(5) | LOGALGID(6) | LOGALGID(7) | LOGALGID(8) | S1(1) | DLYTIME(1) | S1(2) | DLYTIME(2) | S1(3) | S1(4) | S1(5) | DLYTIME(5) | S1(6) | DLYTIME(6) | S1(7) | DLYTIME(7) | S1(8) | LOGALGID(9) | LOGALGID(10) | LOGALGID(11) | LOGALGID(12) | LOGALGID(13) | LOGALGID(14) | LOGALGID(15) | LOGALGID(16) | NN(001) | GENDESC(1) | PRMDESC(1) | GENDESC(2) | PRMDESC(2) | S1REV(1) | S2(1) | S2REV(1) | S3(1) | S3REV(1) | S1REV(2) | S2(2) | S2REV(2) | S3(2) | S3REV(2) | S1REV(3) | S2(3) | S2REV(3) | S3(3) | S3REV(3) | DLYTIME(8) | R1(1) | R2(1) | DEADBAND(1) | R1(2) | R2(2) | DEADBAND(2) | R1(3) | R2(3) | DEADBAND(3) | LOGALGID(17) | LOGALGID(18) | LOGALGID(19) | LOGALGID(20) | LOGALGID(21) | LOGALGID(22) | LOGALGID(23) | LOGALGID(24)
407 | ALARME3_12_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | C1 | 01 | 3 | 20 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(98) | FL_1_ACH1.FL(99) | FL_1_ACH1.FL(105) | FL_1_ACH1.FL(216) | FL_1_ACH1.FL(321) | --.-- | FL_1_ACH1.FL(323) | FL_1_ACH1.FL(324) | FL_1_ACH1.FL(325) | FL_1_ACH1.FL(326) | FL_1_ACH1.FL(327) | FL_1_ACH1.FL(328) | HOLD | L1 | APSL_089_311.PVFL | FL2 | L2 | A26_5N_311.PVFL | FL2 | L3 | A22_5N_311.PVFL | FL2 | L4 | YT22_5N_311.PVFL | FL2 | L5 | A41_5N_311.PVFL | FL2 | L6 | --.-- | FL1 | L7 | A43_5N_311.PVFL | FL2 | L8 | A44_5N_311.PVFL | FL2 | L9 | A45_5N_311.PVFL | FL2 | L10 | A46_5N_311.PVFL | FL2 | L11 | A48_5N_311.PVFL | FL2 | L12 | A49_5N_311.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
1117 | ALARME3_1_PLC() | HPM | FULL | "ALARMES DE ATB ET AXCH " | " " | " " | AX | 01 | 3 | 1 | -- | "----------------" | 12_8_12 | FL_1_ATB.FL(23) | --.-- | FL_1_ATB.FL(24) | --.-- | --.-- | FL_1_AXCH.FL(165) | FL_1_AXCH.FL(166) | FL_1_AXCH.FL(121) | FL_1_AXCH.FL(122) | FL_1_AXCH.FL(123) | FL_1_AXCH.FL(129) | --.-- | HOLD | L1 | A5_D1_364.PVFL | FL2 | L2 | --.-- | FL1 | L3 | YT2_D4_364.PVFL | FL2 | L4 | --.-- | FL1 | L5 | --.-- | FL1 | L6 | YT18_B4_103.PVFL | FL2 | L7 | SSL19_B4_103.PVFL | FL2 | L8 | LSH240324.PVFL | FL2 | L9 | LSL240324.PVFL | FL2 | L10 | PDSH251324.PVFL | FL2 | L11 | PDSH261324.PVFL | FL2 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
1203 | ALARME3_2_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | AX | 01 | 3 | 3 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(254) | FL_1_ACH1.FL(255) | FL_1_ACH1.FL(100) | FL_1_ACH1.FL(101) | FL_1_ACH1.FL(102) | FL_1_ACH1.FL(103) | FL_1_ACH1.FL(104) | FL_1_ACH1.FL(168) | FL_1_ACH1.FL(169) | FL_1_ACH1.FL(171) | FL_1_ACH1.FL(172) | FL_1_ACH1.FL(173) | HOLD | SO1 | A6_B9_364.PVFL | FL2 | SO2 | A1_W5_324.PVFL | FL2 | L3 | A1_5N_311.PVFL | FL2 | L4 | A30_M4_311.PVFL | FL2 | L5 | A5_5N_311.PVFL | FL2 | L6 | A6_5A_311.PVFL | FL2 | L7 | A8_T2_311.PVFL | FL2 | L8 | LSH010311.PVFL | FL2 | L9 | LSH011311.PVFL | FL2 | L10 | LSH015311.PVFL | FL2 | L11 | LSH016311.PVFL | FL2 | L12 | LSH017311.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | PULSE | PULSE | NULL | NULL | NULL | NULL | NULL | NULL | L1 | 3.000000 | L2 | 3.000000
1293 | ALARME3_3_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | AX | 01 | 3 | 10 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(174) | FL_1_ACH1.FL(175) | FL_1_ACH1.FL(176) | FL_1_ACH1.FL(177) | FL_1_ACH1.FL(178) | FL_1_ACH1.FL(179) | FL_1_ACH1.FL(180) | FL_1_ACH1.FL(182) | FL_1_ACH1.FL(183) | --.-- | FL_1_ACH1.FL(185) | --.-- | HOLD | L1 | LSHH010311.PVFL | FL2 | L2 | LSL010311.PVFL | FL2 | L3 | LSL011311.PVFL | FL2 | L4 | LSL018311.PVFL | FL2 | L5 | LSL019311.PVFL | FL2 | L6 | LSLL010311.PVFL | FL2 | L7 | LSLL011311.PVFL | FL2 | L8 | PSH032311.PVFL | FL2 | L9 | PSH058311.PVFL | FL2 | FL1 | --.-- | FL1 | L11 | PSH059311.PVFL | FL2 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
1379 | ALARME3_4_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | AX | 01 | 3 | 11 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(187) | FL_1_ACH1.FL(188) | FL_1_ACH1.FL(189) | --.-- | FL_1_ACH1.FL(191) | FL_1_ACH1.FL(192) | FL_1_ACH1.FL(193) | FL_1_ACH1.FL(194) | FL_1_ACH1.FL(195) | FL_1_ACH1.FL(196) | FL_1_ACH1.FL(197) | FL_1_ACH1.FL(198) | HOLD | L1 | PSH068311.PVFL | FL2 | L2 | PSH504311.PVFL | FL2 | L3 | SSL102311.PVFL | FL2 | L4 | --.-- | FL1 | L5 | PSHH032311.PVFL | FL2 | L6 | PSHH902311.PVFL | FL2 | L7 | PSHH903311.PVFL | FL2 | L8 | PSHH904311.PVFL | FL2 | L9 | PSHH905311.PVFL | FL2 | L10 | PSL022311.PVFL | FL2 | L11 | PSL023311.PVFL | FL2 | L12 | PSL052311.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
1465 | ALARME3_5_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | AX | 01 | 3 | 12 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(199) | FL_1_ACH1.FL(200) | FL_1_ACH1.FL(201) | FL_1_ACH1.FL(202) | FL_1_ACH1.FL(205) | FL_1_ACH1.FL(206) | FL_1_ACH1.FL(207) | FL_1_ACH1.FL(208) | FL_1_ACH1.FL(209) | FL_1_ACH1.FL(210) | FL_1_ACH1.FL(211) | FL_1_ACH1.FL(212) | HOLD | L1 | PSL060311.PVFL | FL2 | L2 | PSL067311.PVFL | FL2 | L3 | PSL400311.PVFL | FL2 | L4 | PSL504311.PVFL | FL2 | L5 | SSL901311.PVFL | FL2 | L6 | SSL923311.PVFL | FL2 | L7 | SSL924311.PVFL | FL2 | L8 | TSH821311.PVFL | FL2 | L9 | TSHH819311.PVFL | FL2 | L10 | TSHH820311.PVFL | FL2 | L11 | TSL804311.PVFL | FL2 | L12 | URG_C224.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
1643 | ALARME3_6_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | AX | 01 | 3 | 13 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(213) | FL_1_ACH1.FL(220) | FL_1_ACH1.FL(221) | FL_1_ACH1.FL(257) | FL_1_ACH1.FL(218) | FL_1_ACH1.FL(228) | FL_1_ACH1.FL(230) | FL_1_ACH1.FL(217) | FL_1_ACH1.FL(219) | FL_1_ACH1.FL(222) | FL_1_ACH1.FL(276) | FL_1_ACH1.FL(161) | HOLD | L1 | URG_SILO.PVFL | FL2 | L2 | YT31_5N_311.PVFL | FL2 | L3 | YT32_5N_311.PVFL | FL2 | L4 | PSHH900311.PVFL | FL2 | SO1 | YT090311.PVFL | FL2 | L6 | PSH042311.PVFL | FL2 | L7 | PSL048311.PVFL | FL2 | L8 | FSL004311.PVFL | FL2 | L9 | SSL042311.PVFL | FL2 | L10 | YT001311.PVFL | FL2 | L11 | LSH101311.PVFL | FL2 | L12 | LSH050109.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NOT | NULL | NULL | NULL | NULL | NULL | NULL | NULL | L5
3187 | DIGITAL_OUTPUT() | HPM | FULL | "DO VERS EQUIPEMENTS " | " " | " " | C1 | 01 | 3 | 14 | -- | "----------------" | 12_8_12 | FT040A311.PVLLFL | FT040B311.PVLLFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | FLL040A311.SO | FL2 | L2 | FLL040B311.SO | FL2 | L3 | --.-- | FL1 | L4 | --.-- | FL1 | L5 | --.-- | FL1 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3463 | PATCHOUT3_1() | HPM | COMPONNT | "TRANSFERT OUTPUT " | " " | " " | AX | 01 | 3 | 2 |  |  | 12_8_12 | LC001311.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | OP001311.OP | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | [17 empty] | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3947 | ALARME3_7_PLC() | HPM | FULL | "ALARMES DE ASAE " | " " | " " | AX | 01 | 3 | 16 | -- | "----------------" | 12_16_8 | FL_1_ASAE.FL(49) | FL_1_ASAE.FL(50) | FL_1_ASAE.FL(51) | FL_1_ASAE.FL(57) | FL_1_ASAE.FL(58) | FL_1_ASAE.FL(68) | FL_1_ASAE.FL(69) | FL_1_ASAE.FL(70) | --.-- | --.-- | --.-- | --.-- | HOLD | SO5 | A9_URG0_364.PVFL | FL2 | SO6 | A7_6A_364.PVFL | FL2 | SO3 | A2_K2_364.PVFL | FL2 | L4 | YT001364.PVFL | FL2 | L5 | YT002364.PVFL | FL2 | SO4 | A10_1A_4_364.PVFL | FL2 | SO8 | A10_1A_5_364.PVFL | FL2 | L8 | A7_1A_3_364.PVFL | FL2 | [12 empty] | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NOT | NOT | NOT | NOT | PULSE | PULSE | PULSE | NOT | L1 |  | L2 |  | L3 | L6 | SO1 | 3.000000 | SO2 | 3.000000 | SO3 | 3.000000 | L7 | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
4088 | FL3_1_VERS_ACH8() | HPM | FULL | "TRANSFERT FLAG VERS PLC " | " " | " " | MZ | 01 | 3 | 7 | -- | "----------------" | 12_8_12 | PC060321.PVLOFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | PL060321.SO | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
4174 | FL3_1_VERS_ACH1() | HPM | FULL | "TRANSFERT FLAG VERS PLC " | " " | " " | EA | 01 | 3 | 8 | -- | "----------------" | 12_8_12 | PC023324.PVLOFL | FT003311.PVHHFL | LC012311.PVLLFL | PC041A311.PVLOFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | PL023324.SO | FL2 | L2 | FH003311.SO | FL2 | L3 | LLL012311.SO | FL2 | L4 | PL041A311.SO | FL2 | L5 | --.-- | FL1 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
4481 | PATCHOUT3_3() | HPM | FULL | "TRANSFERT DE SIGNAUX " | " " | " " | AX | 01 | 3 | 23 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(135) | PATCHOUT3_3.NN(1) | SC009311.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L3 | SU009311.OP | SO1 | L2 | SU009311.OP | SO2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NULL | NULL | NULL | NULL | NULL | NULL | L1 |  | SO1 | [18 empty] | 0.000000
5239 | SELECT_GAZ_HUILE() | HPM | FULL | "SELECTEUR GAZ / HUILE " | "C1 " | " " | C1 | 01 | 3 | 9 | -- | "----------------" | 12_8_12 | FY004B311.PVCALC | FY004C311.PVCALC | FY005B311.PVCALC | FY006A311.PVCALC | HS005_006311.PVFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | FY004D311.PV | SO1 | L2 | FY004D311.PV | SO2 | L3 | FY004G311.PV | SO1 | L4 | FY004G311.PV | SO2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 2 | -- | 0 | ENABLE | HIGH | " " | NONE | HIGH | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NULL | NULL | NULL | NULL | NULL | NULL | L5 |  | SO1 | [19 empty] | "GAZ " | SO1 | "HUILE " | SO2
7926 | TRACKINGS_3_1() | HPM | FULL | "TRACKINGS DU HPM_3 " | " " | " " | AX | 01 | 3 | 15 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(235) | FFC004311.OP | VC005311.PVFL | FFC005311.OP | FFC006311.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L2 | FZ004A_B311.OP | SO1 | NN2 | FZ004A_B311.OP | SO2 | NN1 | FZ004A_B311.OP | SO3 | L4 | FV005311.OP | SO4 | NN2 | FV005311.OP | SO5 | L5 | FV006311.OP | SO4 | NN3 | FV006311.OP | SO5 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOR | AND | AND | NOT | NOT | NULL | NULL | NULL | L1 |  | FL1 |  | L1 | L3 | SO4 | [14 empty] | 100.0000 NN(002)=0.000000 NN(003)=7.000000 |  |  |  |  | OFF | FL1 | OFF | FL1 | OFF | OFF | L1 | ON | FL2 | OFF | OFF | L3 | ON | FL2 | OFF
9700 | ALARME3_8_PLC() | HPM | FULL | "ALARMES DE ASAE " | " " | " " | AX | 01 | 3 | 17 | -- | "----------------" | 12_8_12 | LI004364.PVLLFL | FL_1_ASAE.FL(63) | FL_1_ASAE.FL(72) | FL_1_ASAE.FL(67) | FL_1_ASAE.FL(73) | FL_1_ASAE.FL(65) | FL_1_ASAE.FL(66) | FL_1_ASAE.FL(62) | FL_1_ASAE.FL(77) | --.-- | --.-- | --.-- | HOLD | L1 | LLL004364.PVFL | FL2 | L2 | LLL005364.PVFL | FL2 | L3 | WSH068364.PVFL | FL2 | L4 | PSL499364.PVFL | FL2 | SO1 | A7_1A_7_364.PVFL | FL2 | SO6 | A3_6A_3_364.PVFL | FL2 | SO7 | A3_6A_2_364.PVFL | FL2 | SO8 | A5_1A_1_364.PVFL | FL2 | SO4 | F4_URGO_D17.PVFL | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NOT | NOT | NOT | NOT | NULL | PULSE | PULSE | PULSE | L5 |  | L6 |  | L7 | L9 |  |  | SO2 | 3.000000 | SO3 | 3.000000 | L8 | [28 empty] | 3.000000
10453 | ALARME3_9_PLC() | HPM | FULL | "ALARMES DE ASAE " | " " | " " | AX | 01 | 3 | 18 | -- | "----------------" | 12_8_12 | FL_1_ASAE.FL(77) | FL_1_ASAE.FL(78) | FL_1_ASAE.FL(79) | FL_1_ASAE.FL(80) | FL_1_ASAE.FL(81) | FL_1_ASAE.FL(82) | FL_1_ASAE.FL(83) | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | SO1 | A4_URGO_D17_364.PVFL | FL2 | SO2 | HS100364.PVFL | FL2 | SO3 | HS200364.PVFL | FL2 | SO4 | YT310364.PVFL | FL2 | SO5 | LSH104364.PVFL | FL2 | SO6 | LSH204364.PVFL | FL2 | SO7 | YT320364.PVFL | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NOT | NOT | NOT | NOT | NOT | NOT | NOT | NULL | L1 |  | L2 |  | L3 | L4 | L5 |  | L6 |  | L7
10645 | INIT3_1() | HPM | COMPONNT | "INITIALISE UN CONTROLE " | " " | " " | AX | 01 | 3 | 6 |  |  | 12_8_12 | FL_1_ACH1.FL(165) | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | SO1 | SC944103.CTRLINIT | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | [17 empty] | NOT | NULL | NULL | NULL | NULL | NULL | NULL | NULL | L1
11617 | ALARME3_10_PLC() | HPM | FULL | "ALARMES DE AXCH " | " " | " " | AX | 01 | 3 | 19 | -- | "----------------" | 12_16_8 | FL_1_AXCH.FL(141) | FL_1_AXCH.FL(142) | LC010324.PVLLFL | FL_1_AXCH.FL(189) | FL_1_AXCH.FL(190) | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | SO5 | A2_4B_324.PVFL | FL2 | SO6 | A5_5B_324.PVFL | FL2 | L3 | FL_1_AXCH.FL(145) | FL2 | SO3 | YT083311.PVFL | FL2 | SO4 | YT080310.PVFL | FL2 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | [12 empty] | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NOT | NOT | NOT | NOT | PULSE | PULSE | NULL | NULL | L1 |  | L2 |  | L4 | L5 | SO1 | 3.000000 | SO2 | 3.000000 |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
12056 | PATCHOUT3_2() | HPM | FULL | "TRANSFERT DE SIGNAUX " | " " | " " | AX | 01 | 3 | 4 | -- | "----------------" | 12_8_12 | NN_3_AXCH.NN(10) | LC093311.OP | --.-- | --.-- | PATCHOUT3_2.NN(2) | PATCHOUT3_2.NN(1) | FL_1_ACH1.FL(131) | FL_1_ACH1.FL(132) | FL_1_ACH1.FL(133) | FL_1_ACH1.FL(135) | --.-- | --.-- | HOLD | L1 | KC14B2D6_366SP.PV | FL2 | L2 | SU093311.OP | SO4 | L3 | --.-- | FL1 | L4 | --.-- | FL1 | L6 | I_P093311.OP | SO1 | L5 | I_P093311.OP | SO2 | L2 | I_P093311.OP | SO3 | L6 | SU093311.OP | SO5 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | OR | OR | OR | NOT | NOT | NULL | NULL | NULL | L7 |  | L8 |  | L10 | L10 | SO4 | [14 empty] | 100.0000 NN(002)=0.000000 |  |  |  |  | OFF | L9 | OFF | FL1 | OFF | OFF | FL1 | OFF | FL1 | OFF | OFF | FL1 | OFF | FL1 | OFF
13147 | ALARME3_11_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | C1 | 01 | 3 | 5 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(337) | FL_1_ACH1.FL(338) | FL_1_ACH1.FL(339) | FL_1_ACH1.FL(340) | FL_1_ACH1.FL(341) | FL_1_ACH1.FL(342) | FL_1_ACH1.FL(343) | FL_1_ACH1.FL(281) | FL_1_ACH1.FL(282) | FL_1_ACH1.FL(283) | FL_1_ACH1.FL(112) | FL_1_ACH1.FL(184) | HOLD | L1 | SSL094311.PVFL | FL2 | L2 | SSL095311.PVFL | FL2 | L3 | SSL096311.PVFL | FL2 | L4 | SSL097311.PVFL | FL2 | L5 | LSH113A311.PVFL | FL2 | L6 | LSH114A311.PVFL | FL2 | L7 | SSL925311.PVFL | FL2 | L8 | PSH920311.PVFL | FL2 | L9 | PSH921311.PVFL | FL2 | L10 | SSL922311.PVFL | FL2 | L11 | PDSH026311.PVFL | FL2 | L12 | YS926311.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
14025 | ALARME3_13_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | C1 | 01 | 3 | 21 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(344) | --.-- | FL_1_ACH1.FL(346) | FL_1_ACH1.FL(347) | FL_1_ACH1.FL(348) | FL_1_ACH1.FL(349) | FL_1_ACH1.FL(350) | FL_1_ACH1.FL(231) | FL_1_ACH1.FL(203) | FL_1_ACH1.FL(204) | FL_1_ACH1.FL(170) | FL_1_ACH1.FL(181) | HOLD | L1 | YT41_5N_311.PVFL | FL2 | L2 | --.-- | FL1 | L3 | YT43_5N_311.PVFL | FL2 | L4 | YT44_5N_311.PVFL | FL2 | L5 | YT45_5N_311.PVFL | FL2 | L6 | YT46_5N_311.PVFL | FL2 | L7 | YT47_5N_311.PVFL | FL2 | L8 | PSL031311.PVFL | FL2 | L9 | PSL499311.PVFL | FL2 | L10 | PSL041A311.PVFL | FL2 | L11 | LSH111A311.PVFL | FL2 | L12 | LSH112A311.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
14210 | ALARME3_14_PLC() | HPM | FULL | "ALARMES DE ACH1 " | " " | " " | C1 | 01 | 3 | 24 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(97) | FL_1_ACH1.FL(186) | FL_1_ACH1.FL(214) | FL_1_ACH1.FL(215) | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | LSH111B311.PVFL | FL2 | L2 | LSH112B311.PVFL | FL2 | L3 | LSH113B311.PVFL | FL2 | L4 | LSH114B311.PVFL | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
14472 | TRACKINGS_3_2() | HPM | FULL | "TRACKINGS DU HPM_3 " | " " | " " | LG | 01 | 3 | 22 | -- | "----------------" | 12_8_12 | FL_1_ACH1.FL(109) | PC400311.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L2 | PV400311.OP | SO2 | NN1 | PV400311.OP | SO1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NULL | NULL | NULL | NULL | NULL | NULL | L1 |  | SO1 | [18 empty] | 50.00000
15408 | TRACKING_VENT_C1() | HPM | FULL | "ENTREBARRAGE VENTIL.CH1 " | "C1 " | " " | C1 | 01 | 3 | 25 | -- | "----------------" | 12_8_12 | PC041A311.OP | PC043311.OP | PC042311.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | SO1 | ZY041A311.SO | FL2 | SO2 | ZY043311.SO | FL2 | SO3 | ZY042311.SO | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | LT | LT | LT | NULL | NULL | NULL | NULL | NULL | [21 empty] | 2.000000 NN(002)=5.200000 NN(003)=20.00000 | [20 empty] | L1 | NN1 | 1.000000 | L2 | NN2 | 1.000000 | L3 | NN3 | 1.000000
15833 | PMP_ALIM_EAU_ON() | HPM | FULL | "1/6 POMPE ALIM.EAU FRAIC" | " " | " " | DE | 01 | 3 | 26 | -- | "----------------" | 12_24_4 | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | OFF | FL2 | --.-- | FL1 | FL2 | --.-- | FL1 | FL2 | --.-- | FL1 | FL2 | --.-- | FL1 | [24 empty] | 0 | -- | 0 | ENABLE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL | [13 empty] | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL | [30 empty] | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL

## HPM3 NUMERNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PV | PVFORMAT
3273 | HIER_FQ002324() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRE " | " " | " " | " " | EA | 01 | 3 | 1 | 752182.0 | D1
3286 | HIER_FQ003311() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C1 " | " " | C1 | 01 | 3 | 8 | 713168.0 | D1
3576 | HIER_FQ003321() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | " " | " " | MZ | 01 | 3 | 2 | 0.000000 | D1
3626 | KC14B2D6_366SP() | HPM | COMPONNT | "CONSIGNE GUILLOTINE BOUE" | "minutes " | " " | " " | " " | C1 | 01 | 3 | 27 | 0.000000 | D0
4075 | FQ006_NUIT() | HPM | COMPONNT | "INTEGRATION D'HIER " | "L " | " " | "MZ " | " " | MZ | 01 | 3 | 91 | 12345700 | D1
4396 | HIER_FQ003324() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | " " | " " | EA | 01 | 3 | 3 | 1270.200 | D1
4409 | HIER_FQ003A310() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | " " | " " | DV | 01 | 3 | 4 | 0.000000 | D1
4422 | HIER_FQ003B310() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | " " | " " | DV | 01 | 3 | 5 | 16746.30 | D1
5097 | FY004D311() | HPM | COMPONNT | "DEBIT AIR/GAZ_HUILE CH#1" | "% " | " " | " " | " " | C1 | 01 | 3 | 6 | 8.071500 | D1
5110 | FY004G311() | HPM | COMPONNT | "DEBIT AIR/GAZ_HUILE CH#1" | "% " | " " | " " | " " | C1 | 01 | 3 | 7 | 0.009468 | D1
8381 | HIER_FQ003201() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 50 | 415166.0 | D1
8626 | HIER_FQ003205() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 51 | 17971.30 | D1
8639 | HIER_FQ003270() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 52 | 0.000000 | D1
8652 | HIER_FQ003280() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 53 | 0.000000 | D1
8665 | HIER_FQ003281() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 54 | 0.000000 | D1
8678 | HIER_FQ376213() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 55 | 0.000000 | D1
8691 | HIER_FQ376273() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 56 | 104908.0 | D1
8704 | HIER_FQ402254() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 57 | 0.000000 | D1
8717 | HIER_FQ402274() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 58 | 625623.0 | D1
8730 | HIER_FQ404274() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 59 | 126403.0 | D1
8743 | HIER_FQ426264() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 60 | -------- | D1
8756 | HIER_FQ427214() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 61 | 51651.70 | D1
8769 | HIER_FQ402224() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 62 | 0.000000 | D1
8782 | HIER_FQ427244() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 63 | -------- | D1
8795 | HIER_FQ427264() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 64 | 438600.0 | D1
8808 | HIER_FQ428214() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 65 | 18462.00 | D1
8821 | HIER_FQ428264() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 66 | 125583.0 | D1
8834 | HIER_FQ494274() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 67 | 0.000000 | D1
8847 | HIER_FQ943500() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 68 | 0.000000 | D1
8860 | HIER_FQ003140() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 69 | 93894.60 | D1
9308 | HIER_FQ753120() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 70 | 0.000000 | D1
9321 | HIER_FQ753121() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 71 | 5554.520 | D1
9334 | HIER_FQ753122() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 72 | 5554.520 | D1
9347 | HIER_FQ753A130() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 73 | 8373.640 | D1
9360 | HIER_FQ753B130() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 74 | 17710400 | D1
9373 | HIER_FQ753C130() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 75 | 796482.0 | D1
9386 | HIER_FQ753A140() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 76 | 3907.360 | D1
9399 | HIER_FQ753B140() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 77 | 309958.0 | D1
9412 | HIER_FQ753A151() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 78 | 0.000000 | D1
9425 | HIER_FQ753B151() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 79 | 0.000000 | D1
9438 | HIER_FQ753270() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 80 | 9880820 | D1
9451 | HIER_FQ753280() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 81 | 156868.0 | D1
9464 | HIER_FQ753A290() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 82 | 155699.0 | D1
9477 | HIER_FQ753B290() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 83 | 1531.560 | D1
9490 | HIER_FQ753500() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRES " | " " | "DV " | " " | DV | 01 | 3 | 84 | 0.000000 | D1
9555 | HIER_FQ003122() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 9 | 0.000000 | D0
9641 | HIER_FQ003364() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3/m " | " " | "CE " | " " | CE | 01 | 3 | 10 | 47025400 | D1
10084 | HIER_FQ040282() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 85 | 0.000000 | D1
10097 | HIER_FQ040290() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 86 | 0.000000 | D1
10110 | HIER_FQ040300() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 87 | 0.000000 | D1
10123 | HIER_FQ050311() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 13 | 0.000000 | D1
10136 | HIER_FQ201A289() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 88 | 75370.00 | D1
10149 | HIER_FQ201B289() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 89 | 66730.00 | D1
10162 | HIER_FQ790500() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 90 | 0.000000 | D1
10231 | HIER_FQ006321() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "MZ " | " " | MZ | 01 | 3 | 11 | 76832700 | D0
10273 | HIER_FQ006311() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C1 " | " " | C1 | 01 | 3 | 12 | 0.000000 | D1
11789 | BOUE_12_8() | HPM | COMPONNT | "BRULAGE BOUE ETAPE 12_8 " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 14 | 0.000000 | D1
11802 | BOUE_8_4() | HPM | COMPONNT | "BRULAGE BOUE ETAPE 8_4 " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 15 | 0.000000 | D1
11815 | BOUE_4_12() | HPM | COMPONNT | "BRULAGE BOUE ETAPE 4_12 " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 16 | 0.000000 | D1
11828 | HIER_BOUE_12_8() | HPM | COMPONNT | "BRULAGE BOUE HIER 12_8 " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 17 | 0.000000 | D1
11841 | HIER_BOUE_8_4() | HPM | COMPONNT | "BRULAGE BOUE HIER 8_4 " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 18 | 0.000000 | D1
11854 | HIER_BOUE_4_12() | HPM | COMPONNT | "BRULAGE BOUE HIER 4_12 " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 19 | 0.000000 | D1
11867 | ECORCE_12_8() | HPM | COMPONNT | "TONNAGE ECORCE 12_8 " | "tma " | " " | " " | " " | AX | 01 | 3 | 20 | 54.28770 | D1
11880 | ECORCE_8_4() | HPM | COMPONNT | "TONNAGE ECORCE 8_4 " | "tma " | " " | " " | " " | AX | 01 | 3 | 21 | 38.82350 | D1
11893 | ECORCE_4_12() | HPM | COMPONNT | "TONNAGE ECORCE 4_12 " | "tma " | " " | " " | " " | AX | 01 | 3 | 22 | 0.000000 | D1
11906 | HIER_ECORCE_12_8() | HPM | COMPONNT | "HIER TONNAGE ECORCE 12_8" | "tma " | " " | " " | " " | AX | 01 | 3 | 23 | 49.18120 | D1
11919 | HIER_ECORCE_8_4() | HPM | COMPONNT | "HIER TONNAGE ECORCE 8_4 " | "tma " | " " | " " | " " | AX | 01 | 3 | 24 | 55.17920 | D1
11932 | HIER_ECORCE_4_12() | HPM | COMPONNT | "HIER TONNAGE ECORCE 4_12" | "tma " | " " | " " | " " | AX | 01 | 3 | 25 | 43.21790 | D1
11985 | PO311310() | HPM | COMPONNT | "POSITION VALVE " | "% " | " " | " " | " " | AX | 01 | 3 | 26 | -5.00000 | D1
12917 | FI003310() | HPM | COMPONNT | "DEBIT VAP.APPOINT CALCUL" | "Kg/H " | " " | "DV " | " " | DV | 01 | 3 | 28 | 0.000000 | D0
12978 | HIER_FQ003310() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | " " | " " | DV | 01 | 3 | 29 | 16747.40 | D0
12991 | HIER_FQ006A321() | HPM | COMPONNT | "PART.SUP.HIER_FQ006321 " | "KG " | " " | "MZ " | " " | MZ | 01 | 3 | 30 | 7683.000 | D0
13004 | HIER_FQ006B321() | HPM | COMPONNT | "PART.INF.HIER_FQ0063 " | "KG " | " " | "MZ " | " " | MZ | 01 | 3 | 31 | 2672.000 | D0
14694 | HIER_T_BOUE_12_8() | HPM | COMPONNT | "BRULAGE BOUE HIER 12_8 " | "TONNES " | " " | " " | " " | AX | 01 | 3 | 32 | 0.000000 | D2
14707 | HIER_T_BOUE_8_4() | HPM | COMPONNT | "BRULAGE BOUE HIER 8_4 " | "TONNES " | " " | " " | " " | AX | 01 | 3 | 33 | 0.000000 | D2
14720 | HIER_T_BOUE_4_12() | HPM | COMPONNT | "BRULAGE BOUE HIER 4_12 " | "TONNES " | " " | " " | " " | AX | 01 | 3 | 34 | 0.000000 | D2
14733 | TONNES_BOUE_12_8() | HPM | COMPONNT | "BRULAGE BOUE 12_8 " | "TONNES " | " " | " " | " " | AX | 01 | 3 | 35 | 0.000000 | D2
14746 | TONNES_BOUE_8_4() | HPM | COMPONNT | "BRULAGE BOUE 8_4 " | "TONNES " | " " | " " | " " | AX | 01 | 3 | 36 | 0.000000 | D2
14759 | TONNES_BOUE_4_12() | HPM | COMPONNT | "BRULAGE BOUE 4_12 " | "TONNES " | " " | " " | " " | AX | 01 | 3 | 37 | 0.000000 | D2

## HPM3 PRMODNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | USERID | STRLEN | SEQSLTSZ | CNTLLOCK | SPLOCK | RSTROPT | ACP | CLBACK | SEQPR | TIME(001) | KEYWORD | MODNUM | EXTDATA | IOPNUM | FTANUM | DEVADDR | SCANPRI | AUXDATA1 | AB_DATA1 | AUXDATA2 | AB_DATA2 | AUXDATA3 | AB_DATA3 | AUXDATA4 | AB_DATA4 | FLSTIX | NFLAG | NNSTIX | NNUMERIC | STRSTIX | NSTRING | TIMESTIX | NTIME | FLDESC | NNDESC | STRDESC | TIMEDESC | $ADD | NN(001) | NN(005) | NN(009) | NN(013) | FL(0001)
2 | INTEGRE3_2() | HPM | FULL | "TRANFERT INTEGRE.MIDI " | "INTEGRE " | " " | AX | 01 | 3 | 3 | -- | "----------------" | 8 | 10 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-12:55:36"
22 | NN_2_AXCH() | HPM | FULL | "COMM. 30 REGISTRE AXCH " | " " | " " | AX | 01 | 3 | 6 | -- | "----------------" | 8 |  |  | SUPERVIS | [5 empty] | "MODBUS " | 0 | IO_NN | 18 | 1 | 107.0 | LOW | -------- | -------- | 1.500000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 90730 | 30 | 0.000 | 0 | 0.00 | 0 | " " | "COMM.PLC AXCH MODBUS 30 REGISTRE A PARTIR DE 730 A 759 " | " " | " " | ON
546 | INTEGRE3_3() | HPM | FULL | "TRANSFERT INTEGRE.MINUIT" | "INTEGRE " | " " | AX | 01 | 3 | 4 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-12:56:43"
3639 | TRACK3_1() | HPM | FULL | "TRACKING PROG.CL HPM3 " | " " | " " | C1 | 01 | 3 | 5 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | EMERGNCY
4376 | INTEGRE3_1() | HPM | FULL | "TRANSFERT INTEGRE.MINUIT" | "INTEGRE " | " " | AX | 01 | 3 | 1 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-13:03:33"
10336 | FISCHER_CONVERT() | HPM | FULL | "CONVERSION POUR SYS. PI " | " " | " " | CE | 01 | 3 | 10 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | EMERGNCY | [29 empty] | 31.00000 NN(002)=31.00000 NN(003)=17.00000 NN(004)=2.100000 | 0.250000 NN(006)=0.000000 NN(007)=15.00000 NN(008)=5.700000 | 1.500000 NN(010)=2.200000 NN(011)=100.0000 NN(012)=0.510000 | 599.0000 | ON
10360 | HPM3_PLC_1() | HPM | FULL | "TRANSFERT VERS LES PLC " | "XFER_PLC" | " " | AX | 01 | 3 | 2 | -- | "----------------" | 8 | 20 | OPERATOR | OPERATOR | OFF | -- | 0 | NOACTION
11945 | COMPTEUR3_1() | HPM | FULL | "COMPTEUR GENERAL HPM 3_4" | " " | " " | AX | 01 | 3 | 6 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | RESTART | -- | 0 | NOACTION | " 0-13:15:46"
11965 | COMPTEUR3_2() | HPM | FULL | "COMPTEUR PERTE DE VAPEUR" | " " | " " | AX | 01 | 3 | 8 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | RESTART | -- | 0 | NOACTION | " 0-13:15:48"
12304 | TONNAGE3_1() | HPM | FULL | "TONNAGE BRULAGE ECORCE " | " " | " " | AX | 01 | 3 | 7 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | RESTART | -- | 0 | NOACTION | " 0-13:16:16"
12930 | CALCUL_VAPEUR1() | HPM | FULL | "VAPEUR APPOINT PROG.CL " | " " | " " | DV | 01 | 3 | 9 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | EMERGNCY
15385 | PC312310_RAMPE() | HPM | FULL | "RAMPE SUR PERTE 200 LBS " | "DV " | " " | DV | 01 | 3 | 11 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-15:53:46" | [28 empty] | 200.0000 NN(002)=800.0000 NN(003)=258.0000 NN(004)=120.0000 | 300.0000 NN(006)=900.0000 NN(007)=1000.000 NN(008)=2.000000 | 5.000000 NN(010)=95.00000

## HPM3 REGCLNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | CTLALGID | OVERVAL | BADCTLOP | RCASOPT | NMODE | NMODATTR | MODEPERM | $MODESEL(1) | $MODESEL(5) | $MODESEL(3) | $MODESEL(4) | $BADOCMD | EXTSWOPT | CTLEQN | B | RATE1 | XEUHI | XEULO | NOCINPTS | CISRC(1) | NOCOPTS | CODSTN(1) | OUTIND | OPHILM | OPLOLM | SAFEOP | OPMCHLM | OPROCLM | $OPTOL | $AUXUNIT | $DLBADAL | DLYTIME | $REALARM | BADOCOPT | OPALDB | OPHITP | OPLOTP | BADCTLPR | ALENBST | PVEUHI | PVEULO | PVFORMAT | PVSRCOPT | $MODESEL(2) | SPHILM | SPLOLM | $SPTOL | SP | SPOPT | RBOPT | PIDFORM | PVTRACK | CTLACTN | GAINOPT | K | T1 | T2 | CVEUHI | CVEULO | $ALDLOPT | PVALDB | PVHITP | PVHIPR | $HISELCT | PVLOTP | PVLOPR | $LOSELCT | PVHHTP | PVLLTP | PVROCPTP | PVROCNTP | BADPVPR | DEVHITP | DEVLOTP | CISRC(2) | CODSTN(2) | OPHIPR | PVHHPR | $HHSELCT | PVLLPR | $LLSELCT | PVSGCHTP | RTHILM | RTLOLM | BSHILM | BSLOLM | RATIO | BIAS | PVSOURCE | FFOPT | KFF | OPLOPR
493 | HC094311() | HPM | FULL | "VITESSE CONV. 231 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 0 | 42 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA | 6.000000 | 0.000000 | 100.0000 | 0.000000 | 1 | HC930311.OP | 1 | SU094311.OP | DIRECT | 106.9000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | LOW | ENABLE
790 | PC310310() | HPM | FULL | "PRES.VAP.1310KPA MAITRE " | "KPA " | " " | " " | " " | DV | 01 | 3 | 0 | 1 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | OPERATOR | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PY310310.PVCALC | 0 |  | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 2000.000 | 0.000000 | D1 | ONLYAUTO | ON | 2000.000 | 0.000000 | 0.000000 | 1450.000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 3.000000 | 6.000000 | 0.300000 | 100.0000 | 0.000000 | NONE | ONE | 1520.000 | LOW | CUTOUT | 700.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
872 | PC311310() | HPM | FULL | "PRESSION SOUFFLANTE " | "KPA " | " " | " " | " " | DV | 01 | 3 | 0 | 2 | -- | "----------------" | PID | 25 | NO_SHED | NONE | NONE |  | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PY310310.PVCALC | 1 | PV311310.OP | DIRECT | 100.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 2000.000 | 0.000000 | D1 | ONLYAUTO | ON | 2000.000 | 0.000000 | 0.000000 | 1560.000 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 6.000000 | 1.000000 | 0.000000 |  |  | NONE | ONE | 1500.000 | LOW | CUTOUT | 850.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
952 | PC312310() | HPM | FULL | "PRESSION VAPEUR 800 KPA " | "KPA " | " " | " " | " " | DV | 01 | 3 | 0 | 3 | -- | "----------------" | PID | 25 | NO_SHED | RSP | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | PY312310.PVCALC | 2 | I_P312A310.OP | DIRECT | 105.0000 | -6.90000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 1700.000 | 0.000000 | D1 | ONLYAUTO | ON | 1700.000 | 0.000000 | 0.000000 | 800.0000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 8.500000 | 10.00000 | 0.000000 |  |  | NONE | ONE | 890.0000 | LOW | CUTOUT | 650.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | PC312310_RAMPE.NN(3) | I_P312B310.OP
1035 | PC313310() | HPM | FULL | "PRESSION VAPEUR 210 KPA " | "KPA " | " " | " " | " " | DV | 01 | 3 | 0 | 4 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | OPERATOR | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PY313310.PVCALC | 2 | I_P313A310.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 400.0000 | 0.000000 | D1 | ONLYAUTO | ON | 400.0000 | 0.000000 | 0.000000 | 210.0000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 3.000000 | 2.000000 | 0.000000 |  |  | NONE | ONE | 275.0000 | LOW | CUTOUT | 190.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- |  | I_P313B310.OP
1730 | LC001321() | HPM | FULL | "NIVEAU RESERVOIR MAZOUT " | "% " | " " | " " | " " | MZ | 01 | 3 | 0 | 5 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | LT001321.PV | 1 | LV001321.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | 60.00000 | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 80.00000 | NONE | NORATBI | INTERACT | NOTRACK | REVERSE | LIN | 7.000000 | 7.500000 | 0.000000 |  |  | NONE | ONE | 85.00000 | LOW | CUTOUT | 70.00000 | LOW | CUTOUT | 90.00000 | 65.00000 | -------- | -------- | LOW | -------- | -------- |  |  | LOW | NOACTION | CUTOUT | NOACTION | CUTOUT | --------
1863 | PC060321() | HPM | FULL | "PRES. MAZOUT CHAUDIERES " | "KPA " | " " | " " | " " | MZ | 01 | 3 | 0 | 6 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT060321.PV | 1 | PV060321.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 2000.000 | 0.000000 | D1 | ONLYAUTO | ON | 2000.000 | 0.000000 | 0.000000 | 6.870150 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 0.100000 | 0.010000 | 0.000000 |  |  | NONE | ONE | 1800.000 | LOW | CUTOUT | 1380.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
2008 | TC804321() | HPM | FULL | "TEMP. MAZOUT CHAUDIERES " | "DEGC " | " " | " " | " " | MZ | 01 | 3 | 0 | 7 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | TT804321.PV | 1 | TV804321.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 150.0000 | 0.000000 | D1 | ONLYAUTO | ON | 150.0000 | 0.000000 | 0.000000 | 43.79010 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 3.030000 | 0.500000 |  |  | NONE | ONE | 130.0000 | LOW | CUTOUT | 90.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
2290 | LC001324() | HPM | FULL | "NIVEAU RES. DEGAZEUR " | "% " | " " | " " | " " | EA | 01 | 3 | 0 | 8 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | LY001324.PVCALC | 2 | I_P001A324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 60.00000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 7.500000 | 10.11000 | 0.000000 |  |  | NONE | ONE | 70.00000 | LOW | CUTOUT | 53.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- |  | I_P001B324.OP
2372 | LC010324() | HPM | FULL | "NIVEAU RES. CONDENSE " | "% " | " " | " " | " " | EA | 01 | 3 | 0 | 21 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | LY010324.PVCALC | 2 | I_P010A324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 60.00000 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 5.000000 | 1.500000 | 0.000000 |  |  | NONE | THREE | 75.00000 | LOW | CUTOUT | 53.00000 | LOW | CUTOUT | -------- | 50.00000 | -------- | -------- | LOW | -------- | -------- |  | I_P010B324.OP |  |  |  | LOW | CUTOUT | --------
2457 | LC011324() | HPM | FULL | "NIV.RES.VIDANGE CONTINUE" | "% " | " " | " " | " " | EA | 01 | 3 | 0 | 9 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | LT011324.PV | 1 | LV011324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 50.00000 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 5.000000 | 2.000000 | 0.000000 |  |  | NONE | ONE | 80.00000 | LOW | CUTOUT | 20.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
2538 | PC022324() | HPM | FULL | "PRESSION EAU CHAUFFERIE " | "KPA " | " " | " " | " " | EA | 01 | 3 | 0 | 10 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT022324.PV | 1 | PV022324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 1000.000 | 0.000000 | D1 | ONLYAUTO | ON | 1000.000 | 0.000000 | 0.000000 | 500.0000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.065000 | 0.030000 | 0.000000 |  |  | NONE | ONE | 700.0000 | LOW | CUTOUT | 350.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
2619 | PC023324() | HPM | FULL | "PRES.EAU ALIM.CHAUDIERES" | "KPA " | " " | " " | " " | EA | 01 | 3 | 0 | 22 | -- | "----------------" | PID | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT023324.PV | 1 | PV023324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 3500.000 | 0.000000 | D1 | ONLYAUTO | ON | 3500.000 | 0.000000 | 0.000000 | 3218.950 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 6.000000 | 0.250000 | 0.000000 |  |  | NONE | ONE | 3400.000 | LOW | CUTOUT | 2350.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
2700 | PC030324() | HPM | FULL | "PRESSION DEGAZEUR " | "KPA " | " " | " " | " " | EA | 01 | 3 | 0 | 11 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PY030324.PVCALC | 2 | I_P030A324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 200.0000 | 0.000000 | D1 | ONLYAUTO | ON | 200.0000 | 0.000000 | 0.000000 | 70.00000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.950000 | 2.000000 | 0.050000 |  |  | NONE | ONE | 135.0000 | LOW | CUTOUT | 20.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- |  | I_P030B324.OP
2782 | FFC080324() | HPM | FULL | "DEBIT PHOSPHATE VS E.F. " | "ml / min" | " " | " " | " " | EA | 01 | 3 | 0 | 23 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FT080324.PV | 1 | SU080324.OP | DIRECT | 100.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 34.15000 | 0.000000 | D2 | ONLYAUTO | ON | 15.75000 | 0.000000 | 0.000000 | 0.016035 | NONE | FIXRATBI | INTERACT | NOTRACK | REVERSE | LIN | 0.500000 | 0.100000 | 0.000000 |  |  | NONE | FIVE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | -------- | FY020A324.PVCALC | [7 empty] | 10.00000 | 1.000000 | 50.00000 | -50.0000 | 1.000000 | 0.000000
2902 | PC002A364() | HPM | FULL | "PRES. EAU MOULIN (VALVE)" | "KPA " | " " | " " | " " | DE | 01 | 3 | 0 | 26 | -- | "----------------" | PID | 25 | NO_SHED | NONE | NONE |  | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT002364.PV | 1 | PV002A364.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | DISABLE | 700.0000 | 0.000000 | D1 | ONLYAUTO | ON | 700.0000 | 0.000000 | 0.000000 | 564.0410 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 1.500000 | 0.100000 | 0.000000 |  |  | NONE | ONE | 620.0000 | LOW | CUTOUT | 380.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
2982 | PC002B364() | HPM | FULL | "PRES. EAU MOULIN (POMPE)" | "KPA " | " " | " " | " " | DE | 01 | 3 | 0 | 12 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT002364.PV | 1 | SU002B364.OP | DIRECT | 105.0000 | 70.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 700.0000 | 0.000000 | D1 | ONLYAUTO | ON | 700.0000 | 0.000000 | 0.000000 | 440.0000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.750000 | 0.250000 | 0.000000 |  |  | NONE | ONE | 620.0000 | LOW | CUTOUT | 375.0000 | LOW | CUTOUT | -------- | 350.0000 | -------- | -------- | LOW | -------- | -------- | [5 empty] | HIGH | CUTOUT | --------
3299 | FFC081324() | HPM | FULL | "DEBIT SULPHITE VS E.F. " | "ml / min" | " " | " " | " " | EA | 01 | 3 | 0 | 24 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FT081324.PV | 1 | SU081324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 34.15000 | 0.000000 | D2 | ONLYAUTO | ON | 12.80000 | 0.000000 | 0.000000 | 10.62600 | NONE | FIXRATBI | INTERACT | NOTRACK | REVERSE | LIN | 0.500000 | 0.100000 | 0.000000 |  |  | NONE | FIVE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | -------- | FY020B324.PVCALC | [7 empty] | 100.0000 | 0.010000 | 50.00000 | -50.0000 | 1.500000 | 0.000000
3381 | FFC082324() | HPM | FULL | "DEBIT AMINE+PASSIVATEUR " | "ml / min" | " " | " " | " " | EA | 01 | 3 | 0 | 25 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FT082324.PV | 1 | SU082324.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 34.15000 | 0.000000 | D2 | ONLYAUTO | ON | 33.50000 | 0.000000 | 0.000000 | 0.001924 | NONE | FIXRATBI | INTERACT | NOTRACK | REVERSE | LIN | 0.500000 | 0.100000 | 0.000000 |  |  | NONE | FIVE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | -------- | FY020C324.PVCALC | [7 empty] | 100.0000 | 0.010000 | 50.00000 | -50.0000 | 0.120000 | 0.000000
4593 | AC008311() | HPM | FULL | "CONDUCTIVITE CHAUD. #1 " | "uMHOS " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 28 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | AT008311.PV | 1 | AV008311.OP | DIRECT | 105.0000 | -6.90000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 5000.000 | 0.000000 | D0 | ONLYAUTO | ON | 5000.000 | 0.000000 | 0.000000 | 3100.000 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 10.00000 | 15.00000 | 0.000000 |  |  | NONE | ONE | 4000.000 | LOW | CUTOUT | 2500.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
5045 | HC310311() | HPM | FULL | "MAITRE CHAUDIERE #1" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 27 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA | -10.0000 | 0.000000 | 100.0000 | 0.000000 | 1 | PC310310.OP | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | LOW | ENABLE
5331 | FFC004311() | HPM | FULL | "DEBIT AIR BRULEURS " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 13 | -- | "----------------" | PID | 25 | NO_SHED | RSP | CAS | OPERATOR | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FY004D311.PV | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 6.449010 | NONE | FIXRATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 0.500000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | -------- | FY004F311.PVCALC | [7 empty] | 100.0000 | 0.010000 | 50.00000 | -50.0000 | 1.000000 | 0.000000
5414 | FFC005311() | HPM | FULL | "DEBIT GAZ CHAUDIERE #1" | "m3/h " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 14 | -- | "----------------" | PID | 25 | NO_SHED | RSP | CAS | OPERATOR | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FT005311.PV | 0 |  | DIRECT | 38.00000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 493.0000 | 0.000000 | D1 | ONLYAUTO | ON | 493.0000 | 0.000000 | 0.000000 | 0.093356 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 0.500000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | 493.0000 | LOW | CUTOUT | -------- |  |  | -------- |  | -------- | -------- | LOW | -------- | -------- | FY005C311.PVCALC
5494 | FFC006311() | HPM | FULL | "DEBIT HUILE CHAUDIERE #1" | "kg/h " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 15 | -- | "----------------" | PID | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FT006311.PV | 0 |  | DIRECT | 105.0000 | 7.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 4080.000 | 0.000000 | D1 | ONLYAUTO | ON | 4080.000 | 0.000000 | 0.000000 | 0.000000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 0.500000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | 4080.000 | LOW | CUTOUT | 100.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | FY006B311.PVCALC
5577 | LC001311() | HPM | FULL | "NIVEAU CHAUDIERE #1" | "mmH2O " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 16 | -- | "----------------" | PIDFF | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | LT001311.PV | 1 | FC002311.SP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 400.0000 | -400.000 | D0 | ALL | ON | 400.0000 | -400.000 | 0.000000 | -100.000 | NONE | NORATBI | INTERACT | NOTRACK | REVERSE | LIN | 1.250000 | 11.00000 | 0.000000 |  |  | NONE | ONE | 150.0000 | LOW | CUTOUT | -300.000 | HIGH | CUTOUT | 200.0000 | -350.000 | -------- | -------- | LOW | -------- | -------- | FY003311.PVCALC |  |  | HIGH | CUTOUT | EMERGNCY | CUTOUT | -------- | [6 empty] | AUTO | ADD | 1.000000
5725 | FC002311() | HPM | FULL | "DEBIT EAU CHAUDIERE #1" | "kg/h " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 17 | -- | "----------------" | PID | 75 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | FT002311.PV | 1 | LV001311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 68000.00 | 0.000000 | D0 | ALL | ON | 68000.00 | 0.000000 | 0.000000 | 24893.10 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.400000 | 0.050000 | 0.000000 |  |  | NONE | ONE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | -------- | [14 empty] | AUTO
5801 | SC009311() | HPM | FULL | "VITESSE CONV. A VIS " | "RPM " | " " | "SE " | " " | SE | 01 | 3 | 0 | 29 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 2 | ST009311.PV | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 18.00000 | 0.000000 | D1 | ONLYAUTO | ON | 18.00000 | 0.000000 | 0.000000 | 7.817690 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 0.350000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | -------- | SY009311.PVCALC
5878 | LC012311() | HPM | FULL | "NIV. CHAMBRE DE CONTACT " | "% " | " " | "LG " | " " | LG | 01 | 3 | 0 | 30 | -- | "----------------" | PID | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | LT012311.PV | 1 | SU012A_B311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 28.00000 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 3.500000 | 12.00000 | 0.000000 |  |  | NONE | ONE | 38.00000 | EMERGNCY | CUTOUT | 8.000000 | HIGH | CUTOUT | -------- | 5.000000 | -------- | -------- | LOW | -------- | -------- | [5 empty] | HIGH | CUTOUT | --------
5962 | PC031311() | HPM | FULL | "PRES. VAPEUR ATOMISANTE " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 31 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT031311.PV | 1 | PV031311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 1375.000 | 0.000000 | D1 | ONLYAUTO | ON | 1375.000 | 0.000000 | 0.000000 | 1375.000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 1.000000 | 0.000000 |  |  | NONE | ONE | 1000.000 | HIGH | CUTOUT | 250.0000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
6096 | FC040311() | HPM | FULL | "DEBIT AIR SOUS GRILLE " | "m3/m " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 32 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FY040311.PVCALC | 1 | FZ040A_B311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 1600.000 | 0.000000 | D0 | ONLYAUTO | ON | 1600.000 | 0.000000 | 0.000000 | 725.0000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 2.000000 | 5.000000 | 0.000000 |  |  | NONE | ONE | 1400.000 | LOW | CUTOUT | 300.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | AY088B311.PVCALC
6178 | PC041A311() | HPM | FULL | "PRESSION AIR FORCE " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 33 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT041A311.PV | 1 | PZ041A311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 3.000000 | 0.000000 | D2 | ONLYAUTO | ON | 3.000000 | 0.000000 | 0.000000 | 1.500000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.200000 | 0.150000 | 0.000000 |  |  | NONE | ONE | 2.500000 | LOW | CUTOUT | 0.200000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
6259 | PC042311() | HPM | FULL | "PRESSION FOYER " | "Kpa " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 34 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT042311.PV | 1 | SU042311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 0.075000 | -0.07500 | D3 | ONLYAUTO | ON | 0.075000 | -0.07500 | 0.000000 | 0.012707 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 0.100000 | 0.250000 | 0.000000 |  |  | NONE | ONE | 0.075000 | NOACTION | CUTOUT | -------- |  |  | -------- |  | -------- | -------- | NOACTION | -------- | --------
6337 | PC043311() | HPM | FULL | "PRESSION AIR SUR GRILLE " | "Kpa " | "SECOND. " | "C1 " | " " | C1 | 01 | 3 | 0 | 35 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | OFF | OFF | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT043311.PV | 1 | PZ043311.OP | DIRECT | 105.0000 | 5.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 10.00000 | 0.000000 | D1 | ONLYAUTO | ON | 10.00000 | 0.000000 | 0.000000 | 5.000000 | NONE | NORATBI | INTERACT | NOTRACK | REVERSE | LIN | 0.400000 | 0.500000 | 0.000000 |  |  | NONE | ONE | 10.00000 | LOW | CUTOUT | 1.000000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
6418 | AC080311() | HPM | FULL | "CONTROLE O2 COMBUSTION " | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 37 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 2 | AT080311.PVCALC | 0 |  | DIRECT | 100.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 21.00000 | 0.000000 | D2 | ONLYAUTO | ON | 21.00000 | 0.000000 | 0.000000 | 8.153570 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 7.500000 | 1.500000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | -------- |  |  | 7.000000 | LOW | CUTOUT |  | 6.500000 | -------- | -------- | LOW | -------- | -------- | AY080A311.PVCALC |  |  |  |  | NOACTION | CUTOUT | --------
6501 | SC922311() | HPM | FULL | "VITESSE CONV.CENDRES" | "m/m " | " " | "LG " | " " | LG | 01 | 3 | 0 | 38 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | ST922311.PV | 1 | SU922311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 3.000000 | -0.01000 | D1 | ONLYAUTO | ON | 3.000000 | 0.000000 | 0.000000 | 0.500000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.500000 | 0.400000 | 0.000000 |  |  | NONE | ONE | 3.000000 | LOW | CUTOUT | -------- |  |  | -------- |  | -------- | -------- | LOW | -------- | --------
7742 | PC499303() | HPM | FULL | "AIR INST. EMBALLEUSE " | "kPa " | " " | " " | " " | AX | 01 | 3 | 0 | 39 | -- | "----------------" | PID | 25 | NO_SHED | NONE | NONE |  | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT499303.PV | 1 | PV499303.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 1000.000 | 0.000000 | D1 | ONLYAUTO | ON | 1000.000 | 0.000000 | 0.000000 | 644.5120 | NONE | NORATBI | INTERACT | TRACK | DIRECT | LIN | 1.250000 | 0.200000 | 0.000000 |  |  | NONE | ONE | 700.0000 | HIGH | CUTOUT | 450.0000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
7873 | HC095311() | HPM | FULL | "VITESSE CONV. 232 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 0 | 43 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA | 9.000000 | 0.000000 | 100.0000 | 0.000000 | 1 | HC930311.OP | 1 | SU095311.OP | DIRECT | 106.9000 | -6.90000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | LOW | ENABLE
10546 | SC944103() | HPM | FULL | "VITESSE CONV CAOUTCH.#2 " | "% " | " " | " " | " " | SE | 01 | 3 | 0 | 40 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | SHEDMAN | NONE | EQA |  |  |  |  | 1 | NN_3_AXCH.NN(9) | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 1.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 0.000000 | NONE | NORATBI | INTERACT | TRACK | REVERSE | LIN | 0.500000 | 2.000000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | -------- |  |  | -------- |  |  |  |  | -------- | -------- | LOW | -------- | --------
13068 | LC093311() | HPM | FULL | "NIV. TREMIE ECORCES " | "% " | " " | " " | " " | SE | 01 | 3 | 0 | 20 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | OFF | OFF | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 1 | LT093311.PV | 0 |  | DIRECT | 100.0000 | 17.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 100.0000 | 0.000000 | D1 | ONLYAUTO | ON | 100.0000 | 0.000000 | 0.000000 | 40.00000 | NONE | NORATBI | INTERACT | NOTRACK | REVERSE | LIN | 0.450000 | 30.00000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | 99.00000 | HIGH | CUTOUT | -------- |  |  | -------- |  | -------- | -------- | HIGH | -------- | --------
13279 | HC096311() | HPM | FULL | "VITESSE CONV. 233 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 0 | 44 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA | -3.00000 | 0.000000 | 100.0000 | 0.000000 | 1 | HC930311.OP | 1 | SU096311.OP | DIRECT | 106.9000 | -6.90000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | LOW | ENABLE
13332 | HC097311() | HPM | FULL | "VITESSE CONV. 234 " | "% " | " " | "SE " | " " | SE | 01 | 3 | 0 | 45 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA | -3.00000 | 0.000000 | 100.0000 | 0.000000 | 1 | HC930311.OP | 1 | SU097311.OP | DIRECT | 106.9000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | LOW | ENABLE
13385 | HC098311() | HPM | FULL | "VITESSE GRILLE MOBIL" | "% " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 36 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | NONE |  | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA | 0.000000 | 0.000000 | 100.0000 | 0.000000 | 0 |  | 1 | SU098311.OP | DIRECT | 106.9000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | 105.0000 | 30.00000 | LOW | ENABLE | [37 empty] | LOW | [14 empty] | LOW
13603 | HC930311() | HPM | FULL | "MAITRE ALIM. ECORCES " | "% " | " " | "SE " | " " | SE | 01 | 3 | 0 | 19 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA | 15.00000 | 0.000000 | 100.0000 | 0.000000 | 1 | PC314310.OP | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | 100.0000 | 0.000000 | NOACTION | ENABLE | [37 empty] | LOW | [14 empty] | LOW
14390 | PC400311() | HPM | FULL | "PRESSION AIRLAVEUR A GAZ" | "KPA " | " " | "LG " | " " | LG | 01 | 3 | 0 | 18 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | OFF | OFF | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PT400311.PV | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 1034.000 | 0.000000 | D0 | ONLYAUTO | ON | 1034.000 | 0.000000 | 0.000000 | 700.0000 | NONE | NORATBI | INTERACT | NOTRACK | DIRECT | LIN | 1.000000 | 0.050000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | 700.0000 | LOW | CUTOUT | 450.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
14561 | FC450311() | HPM | FULL | "DEBIT AIR DIST.ECORCES" | "m3/m " | "SECOND. " | "C1 " | " " | C1 | 01 | 3 | 0 | 46 | -- | "----------------" | PID | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FT450311.PV | 1 | FZ450311.OP | DIRECT | 105.0000 | 5.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 99.00000 | 0.000000 | D1 | ONLYAUTO | ON | 99.00000 | 0.000000 | 0.000000 | 47.00000 | NONE | NORATBI | INTERACT | NOTRACK | REVERSE | LIN | 1.200000 | 0.600000 | 0.000000 |  |  | NONE | ONE | 99.00000 | LOW | CUTOUT | 20.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | HC450311.OP
14954 | FC044311() | HPM | FULL | "DEBIT AIR SUR GRILLE " | "M3/MIN " | "SECOND. " | "C1 " | " " | C1 | 01 | 3 | 0 | 41 | -- | "----------------" | PID | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | OFF | ON | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 2 | FY044A311.PVCALC | 1 | FZ044311.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 750.0000 | -10.0000 | D1 | ONLYAUTO | ON | 750.0000 | 0.000000 | 0.000000 | 217.9940 | NONE | FIXRATBI | INTERACT | NOTRACK | REVERSE | LIN | 2.500000 | 0.250000 | 0.000000 |  |  | NONE | ONE | 700.0000 | LOW | CUTOUT | 0.000000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | FY044B311.PVCALC | [7 empty] | 100.0000 | 0.010000 | 50.00000 | -50.0000 | 0.650000 | 0.000000
15274 | PC314310() | HPM | FULL | "PRES.VAP.1310KPA CHAUD#1" | "KPA " | " " | "SE " | " " | DV | 01 | 3 | 0 | 47 | -- | "----------------" | PID | 25 | NO_SHED | NONE | AUTO | OPERATOR | PERMIT | ON | OFF | OFF | OFF | SHEDMAN | NONE | EQA |  |  |  |  | 1 | PY310310.PVCALC | 0 |  | DIRECT | 50.00000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- |  | ENABLE | 2000.000 | 0.000000 | D1 | ONLYAUTO | ON | 2000.000 | 0.000000 | 0.000000 | 1350.000 | NONE | NORATBI | INTERACT | NOTRACK | REVERSE | LIN | 1.250000 | 30.00000 | 0.000000 | 100.0000 | 0.000000 | NONE | ONE | 1450.000 | LOW | CUTOUT | 800.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | --------
15611 | HC088311() | HPM | FULL | "BIAS CONTROLAIR SOUS GRI" | "M3/MIN " | " " | "SE " | " " | SE | 01 | 3 | 0 | 48 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | MAN | OPERATOR | PERMIT | ON | OFF | OFF | OFF | SHEDMAN | NONE | EQA | 10.00000 | 0.000000 | 100.0000 | 0.000000 | 1 | AI088311.PVCALC | 0 |  | DIRECT | 100.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | LOW | ENABLE
15769 | HC450311() | HPM | FULL | "BIAS CONTROLDIST ECORCES" | "M3/M " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 49 | -- | "----------------" | AUTOMAN | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | OFF | OFF | ON | OFF | SHEDMAN | NONE | EQA | 14.69670 | 0.000000 | 100.0000 | 0.000000 | 1 | FY450A311.PVCALC | 0 |  | DIRECT | 106.9000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | HIGH | ENABLE

## HPM3 REGPVNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PVALGID | PVEUHI | PVEULO | PVFORMAT | PVEXEUHI | PVEXEULO | PVCLAMP | TF | PVEQN | ACCTYPE | TIMEBASE | C | RESETVAL | CUTOFFLM | AVTV | AVDEV1TP | PISRC(1) | PRIMMOD | USERID | PVSRCOPT | PVTV | OVERVAL | N | NMIN | FRCPERM | PISRC(2) | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | PVALDB | PVHITP | PVLOTP | PVROCPTP | PVROCNTP | BADPVPR | ALENBST | DEVHITP | C1 | C2 | C3 | C4 | CALCEXP | PISRC(3) | SEGTOT | IN0 | OUT0 | IN1 | OUT1 | IN2 | OUT2 | IN3 | OUT3 | IN4 | OUT4 | IN5 | OUT5 | IN6 | OUT6 | IN7 | OUT7 | IN8 | OUT8 | IN9 | OUT9 | PVCHAR | COMPHILM | COMPLOLM | RP | RT | P0 | T0 | PISRC(4) | D | C5 | C6 | PISRC(5) | PISRC(6) | PVHIPR | $HISELCT | PVLOPR | $LOSELCT | PVHHTP | PVLLTP | PVLLPR | $LLSELCT | PVSGCHTP | PVSOURCE | IN10 | OUT10 | IN11 | OUT11 | IN12 | OUT12 | PVHHPR | $HHSELCT
168 | FQ002324() | HPM | COMPONNT | "DEBIT EAU ADOUCISSEUR " | "LITRE " | " " | " " | " " | EA | 01 | 3 | 0 | 39 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI002324.PV
658 | PY312310() | HPM | FULL | "AVG (PT312A ET PT312B) " | "KPA " | "AVERAGE " | " " | " " | DV | 01 | 3 | 0 | 2 | HILOAVG | 1700.000 | 0.000000 | D1 | 1729.000 | -29.0000 | NOCLAMP | 0.000000 | EQC | [7 empty] | PT312A310.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | PT312B310.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
702 | PY310310() | HPM | FULL | "AVG (PT310A ET PT310B) " | "KPA " | "AVERAGE " | " " | " " | DV | 01 | 3 | 0 | 1 | HILOAVG | 2000.000 | 0.000000 | D1 | 2029.000 | -29.0000 | NOCLAMP | 0.000000 | EQC | [7 empty] | PT310A310.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | PT310B310.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
746 | PY313310() | HPM | FULL | "AVG (PT313A ET PT313B) " | "KPA " | "AVERAGE " | " " | " " | DV | 01 | 3 | 0 | 3 | HILOAVG | 400.0000 | 0.000000 | D1 | 402.9000 | -2.90000 | NOCLAMP | 0.000000 | EQC | [7 empty] | PT313A310.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | PT313B310.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
2089 | LY001324() | HPM | FULL | "AVG (LT001A ET LT001B) " | "% " | "AVERAGE " | " " | " " | EA | 01 | 3 | 0 | 4 | HILOAVG | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | 0.000000 | EQC | [7 empty] | LT001A324.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | LT001B324.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
2133 | LY010324() | HPM | FULL | "AVG (LT010A ET LT010B) " | "% " | "AVERAGE " | " " | " " | EA | 01 | 3 | 0 | 5 | HILOAVG | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | 0.000000 | EQC | [7 empty] | LT010A324.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | LT010B324.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
2246 | PY030324() | HPM | FULL | "AVG (PT030A ET PT030B) " | "KPA " | "AVERAGE " | " " | " " | EA | 01 | 3 | 0 | 6 | HILOAVG | 200.0000 | 0.000000 | D1 | 202.9000 | -2.90000 | NOCLAMP | 0.000000 | EQC | [7 empty] | PT030A324.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | PT030B324.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
3066 | FQ003311() | HPM | COMPONNT | "DEBIT VAPEUR CHAUDIERE#1" | "KG " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 44 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FT003311.PV
4260 | FQ003321() | HPM | COMPONNT | "DEBIT VAPEUR RES. MAZOUT" | "KG " | " " | " " | " " | MZ | 01 | 3 | 0 | 40 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003321.PV
4289 | FQ003324() | HPM | COMPONNT | "DEBIT VAPEUR DEGAZEUR " | "KG " | " " | " " | " " | EA | 01 | 3 | 0 | 41 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003324.PV
4318 | FQ003A310() | HPM | COMPONNT | "DEBIT VAPEUR D'APPOINT " | "KG " | " " | " " | " " | DV | 01 | 3 | 0 | 42 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003A310.PV
4347 | FQ003B310() | HPM | COMPONNT | "DEBIT VAP. APPOINT TOTAL" | "KG " | " " | " " | " " | DV | 01 | 3 | 0 | 43 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003B310.PV
4435 | FY020B324() | HPM | FULL | "CONVERT L/M_ML/MIN FFC08" | "ml / min" | " " | " " | " " | EA | 01 | 3 | 0 | 37 | CALCULTR | 16.66000 | 0.000000 | D2 | 20.00000 | -3.33000 | CLAMP | 0.000000 | [8 empty] | FI020324.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 3 |  |  | FI020324.PVEUHI | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FFC081324.PVEUHI
4765 | FY004A311() | HPM | FULL | "SOMMATEUR " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 7 | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | EQC | [7 empty] | FT004311.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 1 | OFF | FT004311.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
4809 | FY004B311() | HPM | FULL | "CARACTERISATION AIR&GAZ " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 8 | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -30.0000 | NOCLAMP | 0.000000 | [8 empty] | FY004A311.PVCALC | -- | "----------------" | ONLYAUTO | -------- | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 9 | 11.50000 | 9.100000 | 20.00000 | 19.50000 | 29.00000 | 30.10000 | 37.50000 | 40.00000 | 43.50000 | 47.50000 | 52.50000 | 57.50000 | 55.00000 | 60.10000 | 57.50000 | 61.80000 | 60.00000 | 62.50000 | 100.0000 | 63.00000
4868 | FY004C311() | HPM | FULL | "CARACTERISAT. AIR/HUILE " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 9 | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | FY004A311.PVCALC | -- | "----------------" | ONLYAUTO | -------- | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 9 | 11.50000 | 11.50000 | 20.00000 | 20.00000 | 29.00000 | 29.00000 | 37.50000 | 37.50000 | 43.50000 | 43.50000 | 52.50000 | 52.50000 | 55.00000 | 55.00000 | 57.50000 | 57.50000 | 60.00000 | 60.00000 | 100.0000 | 65.00000
4927 | FY005A311() | HPM | COMPONNT | "COMPENSATEUR DE DEBIT " | "m3/h " | " " | " " | " " | C1 | 01 | 3 | 0 | 12 | FLOWCOMP | 3710.000 | 0.000000 | D1 | 4500.000 | -750.000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | FT005311.PV | [8 empty] | PT052311.PV | [13 empty] | 1.000000 | 1.000000 |  |  |  | TT822311.PV | [21 empty] | LINEAR | 1.250000 | 0.800000 | 621.3250 | 323.1500 | 101.3250 | 273.1500
4961 | FY005B311() | HPM | COMPONNT | "CONVERTIR ENG / % " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 13 | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | FT005311.PV | [5 empty] | 2 |  |  | FT005311.PVEUHI | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 "
4989 | FY006A311() | HPM | COMPONNT | "CONVERTIR ENG / % " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 15 | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | FT006311.PV | [5 empty] | 2 |  |  | FT006311.PVEUHI | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 "
5017 | FY005C311() | HPM | COMPONNT | "CONVERTIR % / ENG " | "ENG " | " " | " " | " " | C1 | 01 | 3 | 0 | 14 | CALCULTR | 493.0000 | 0.000000 | D1 | 550.0000 | -50.0000 | NOCLAMP | 0.000000 | [8 empty] | FY004E311.PVCALC | [5 empty] | 2 |  |  | FT005311.PVEUHI | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*P2 "
5123 | FY004E311() | HPM | FULL | "LO SELECTEUR AIR/MAITRE " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 10 | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -30.0000 | NOCLAMP | 0.000000 | EQB | [7 empty] | FY004D311.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 2 | OFF | HC310311.OP | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | HIGH | ENABLE | --------
5167 | FY004F311() | HPM | FULL | "HI SELECT. HUILE/MAITRE" | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 11 | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | EQA | [7 empty] | FY004G311.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 2 | 2 | OFF | HC310311.OP | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | HIGH | ENABLE | --------
5211 | FY006B311() | HPM | COMPONNT | "CONVERTIR % / ENG " | "ENG " | " " | " " | " " | C1 | 01 | 3 | 0 | 16 | CALCULTR | 4080.000 | 0.000000 | D1 | 5000.000 | -1000.00 | NOCLAMP | 0.000000 | [8 empty] | FY004E311.PVCALC | [5 empty] | 2 |  |  | FT006311.PVEUHI | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*P2 "
5667 | FY002311() | HPM | COMPONNT | "CONVERTIR ENG / ENG " | "mmH2O " | " " | " " | " " | C1 | 01 | 3 | 0 | 17 | CALCULTR | 410.0000 | -410.000 | D1 | 500.0000 | -500.000 | NOCLAMP | 0.000000 | [8 empty] | FT002311.PV | [5 empty] | 4 |  |  | FT002311.PVEUHI | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*(P3-P4)+P4 " | LC001311.PVEUHI | [28 empty] | LC001311.PVEULO
5697 | FY003311() | HPM | COMPONNT | "CONVERTIR ENG / % " | "% " | " " | " " | " " | C1 | 01 | 3 | 0 | 18 | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | FT003311.PV | [5 empty] | 2 |  |  | FT003311.PVEUHI | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 "
6043 | FY040311() | HPM | FULL | "SOMMATEUR AIR FORCE " | "m3/MIN " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 27 | SUMMER | 1600.000 | 0.000000 | D0 | 2000.000 | -40.0000 | NOCLAMP | 0.100000 | EQB |  |  | 1.000000 |  |  |  |  | FT040A311.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 6 |  |  | FT040B311.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 1.000000 | 1.000000 | -1.00000 | -1.00000 |  | FC450311.PV | [28 empty] | FI044A311.PV | 0.000000 | -1.00000 | -1.00000 | FI044B311.PV | FY004H311.PVCALC
7845 | HY094_095311() | HPM | COMPONNT | "SOMMATEUR CONV.OUEST\EST" | "% " | " " | " " | " " | SE | 01 | 3 | 0 | 20 | CALCULTR | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | 0.000000 | [8 empty] | HC094311.OP | [5 empty] | 2 |  |  | HC095311.OP | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "(P1+P2)/2 "
8033 | FQ003201() | HPM | COMPONNT | "DEBIT VAPEUR MOULIN A " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 50 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003201.PV
8062 | FQ003205() | HPM | COMPONNT | "DEBIT VAPEUR MOULIN B " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 51 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003205.PV
8091 | FQ003270() | HPM | COMPONNT | "DEBIT VAPEUR MP7 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 52 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003270.PV
8120 | FQ003280() | HPM | COMPONNT | "DEBIT VAPEUR COUCH.SUPER" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 53 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003280.PV
8149 | FQ003281() | HPM | COMPONNT | "DEBIT VAPEUR CUISINE " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 54 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003281.PV
8178 | FQ376213() | HPM | COMPONNT | "DEBIT BOITE VAPEUR MP1 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 55 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI376213.PV
8207 | FQ376273() | HPM | COMPONNT | "DEBIT BOITE VAPEUR MP7 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 56 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI376273.PV
8236 | FQ402254() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA MP5" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 57 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI402254.PV
8265 | FQ402274() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA MP7" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 58 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI402274.PV
8294 | FQ404274() | HPM | COMPONNT | "DEBIT VAPEUR THERMO MP7 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 59 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI404274.PV
8323 | FQ426264() | HPM | COMPONNT | "DEBIT VAPEUR 800 KPA MP6" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 60 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI426264.PV
8352 | FQ427214() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA MP1" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 61 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI427214.PV
8394 | FQ402224() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA MP2" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 62 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI402224.PV
8423 | FQ427244() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA MP4" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 63 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI427244.PV
8452 | FQ427264() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA MP6" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 64 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI427264.PV
8481 | FQ428214() | HPM | COMPONNT | "DEBIT VAPEUR THERMO MP1 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 65 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI428214.PV
8510 | FQ428264() | HPM | COMPONNT | "DEBIT VAPEUR THERMO MP6 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 66 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI428264.PV
8539 | FQ494274() | HPM | COMPONNT | "DEBIT VAPEUR 210 KPA AUX" | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 67 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI494274.PV
8568 | FQ943500() | HPM | COMPONNT | "DEBIT VAPEUR MP10 " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 68 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI943500.PV
8597 | FQ003140() | HPM | COMPONNT | "DEBIT VAPEUR TMP " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 69 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003140.PV
8873 | FQ753120() | HPM | COMPONNT | "DEBIT E.F.MP1234 TAMA C8" | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 70 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753120.PV
8902 | FQ753121() | HPM | COMPONNT | "DEBIT E.F. DEF A_B TAMA" | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 71 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753121.PV
8931 | FQ753122() | HPM | COMPONNT | "DEBIT E.F. DEF A_B TAMA" | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 72 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753121.PV
8960 | FQ753A130() | HPM | COMPONNT | "DEBIT E.F.MP567 TAMB C9 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 73 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753A130.PV
8989 | FQ753B130() | HPM | COMPONNT | "DEBIT E.F.MP567 TAMB C9 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 74 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753B130.PV
9018 | FQ753C130() | HPM | COMPONNT | "DEBIT E.F.MP56 COUCH.9 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 75 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753C130.PV
9047 | FQ753A140() | HPM | COMPONNT | "DEBIT E.F. TMP L1_L2 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 76 | TOTALIZR | 1.000E08 | 0.000000 | D0 | 1.000E08 | 0.000000 | CLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753A140.PV
9076 | FQ753B140() | HPM | COMPONNT | "DEBIT E.F. TMP L3_L4_L5" | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 77 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753B140.PV
9105 | FQ753A151() | HPM | COMPONNT | "DEBIT E.F. KRAFT_GL_AMI" | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 78 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753A151.PV
9134 | FQ753B151() | HPM | COMPONNT | "DEBIT E.F. KRAFT_GL_AMI" | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 79 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753B151.PV
9163 | FQ753270() | HPM | COMPONNT | "DEBIT E.F. MP7 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 80 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753270.PV
9192 | FQ753280() | HPM | COMPONNT | "DEBIT E.F. COUCHEUSE 8 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 81 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753280.PV
9221 | FQ753A290() | HPM | COMPONNT | "DEBIT E.F. COUCHEUSE 9 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 82 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753A290.PV
9250 | FQ753B290() | HPM | COMPONNT | "DEBIT E.F. COUCHEUSE 9 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 83 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753B290.PV
9279 | FQ753500() | HPM | COMPONNT | "DEBIT E.F. MP10 " | "LITRES " | " " | "DE " | " " | DE | 01 | 3 | 0 | 84 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753500.PV
9526 | FQ003122() | HPM | COMPONNT | "DEBIT VAPEUR TAMISAGE A " | "KG " | " " | "DV " | " " | DV | 01 | 3 | 0 | 46 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI427500.PV
9568 | FI003364() | HPM | FULL | "DEBIT E.F. CLARIFICAT. " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 0 | 102 | DATAACQ | 98420.00 | 0.000000 | D0 | 118000.0 | -19700.0 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER1.NN(6) | -- | "----------------" | ONLYAUTO | 35000.00 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | 64000.00 | 11000.00 | -------- | -------- | LOW | ENABLE | [41 empty] | HIGH | CUTOUT | HIGH | CUTOUT | -------- | --------
9612 | FQ003364() | HPM | COMPONNT | "DEBIT E.F. CLARIFICAT. " | "m3/m " | " " | "CE " | " " | CE | 01 | 3 | 0 | 47 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003364.PV
9888 | FQ040282() | HPM | COMPONNT | "DEBIT GAS COUCHEUSE 8 " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 85 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 1.000000 | 0.000000 | -------- | -------- | -------- | FT040282.PV
9916 | FQ040290() | HPM | COMPONNT | "DEBIT GAS COUCHEUSE 9 " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 86 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 1.000000 | 0.000000 | -------- | -------- | -------- | FT040290.PV
9944 | FQ040300() | HPM | COMPONNT | "DEBIT GAS ENTREPOT " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 87 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 100.0000 | 0.000000 | -------- | -------- | -------- | FT040300.PV
9972 | FQ050311() | HPM | COMPONNT | "DEBIT GAS CHAUDIERE #1" | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 88 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 1.000000 | 0.000000 | -------- | -------- | -------- | FT050311.PV
10000 | FQ201A289() | HPM | COMPONNT | "DEBIT GAS USINE MINUIT" | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 89 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 10.00000 | 0.000000 | -------- | -------- | -------- | FT201289.PV
10028 | FQ201B289() | HPM | COMPONNT | "DEBIT GAS USINE MIDI " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 90 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 10.00000 | 0.000000 | -------- | -------- | -------- | FT201289.PV
10056 | FQ790500() | HPM | COMPONNT | "DEBIT GAS MP10 " | "m3 " | " " | "GN " | " " | GN | 01 | 3 | 0 | 91 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | PULSE |  | 1.000000 | 0.000000 | -------- | -------- | -------- | FT790500.PV
10175 | FY004H311() | HPM | COMPONNT | "CONVERTIR % / ENG " | "M3/MIN " | " " | " " | " " | C1 | 01 | 3 | 0 | 31 | CALCULTR | 285.0000 | 0.000000 | D1 | 300.0000 | -10.0000 | NOCLAMP | 0.000000 | [8 empty] | FT004311.PV | [5 empty] | 1 | [16 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1*2.85 "
10202 | FQ006321() | HPM | COMPONNT | "DEBIT MAZOUT RES. MAZOUT" | "KG " | " " | "MZ " | " " | MZ | 01 | 3 | 0 | 48 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI753C140.PV
10244 | FQ006311() | HPM | COMPONNT | "DEBIT HUILE CHAUDIERE #1" | "KG " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 45 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FT006311.PV
10309 | SI25B6109() | HPM | COMPONNT | "VITESSE CONVOYEUR 38" | "% " | " " | " " | " " | SE | 01 | 3 | 0 | 95 | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | NN_3_AXCH.NN(7) | [5 empty] | 1 | [16 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100 "
10402 | FY044A311() | HPM | COMPONNT | "SOMMAT.DEBITAIR SUR GRIL" | "M3/MIN " | " " | "SE " | " " | SE | 01 | 3 | 0 | 96 | CALCULTR | 750.0000 | 0.000000 | D1 | 750.0000 | 0.000000 | NOCLAMP | 0.000000 | [8 empty] | FI044A311.PV | [5 empty] | 2 |  |  | FI044B311.PV | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1+P2 "
10713 | FI753132() | HPM | FULL | "DEBIT E.F. TAMISAGE B " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 0 | 33 | CALCULTR | 80000.00 | 0.000000 | D0 | 80000.00 | 0.000000 | CLAMP | 0.000000 | [8 empty] | FI753A130.PV | -- | "----------------" | ONLYAUTO | 0.000000 | 25 | 4 |  |  | FI753B130.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "(P1+P2)-(P3+P4) " | FI753270.PV | [28 empty] | FI753C130.PV
10760 | FI753201() | HPM | FULL | "DEBIT E.F. MP.1-2-4 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 0 | 34 | CALCULTR | 20000.00 | 0.000000 | D0 | 20000.00 | 0.000000 | CLAMP | 0.000000 | [8 empty] | FI753120.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 3 |  |  | FI753122.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1-(P2+P3) " | FI753280.PV
10806 | FI753205() | HPM | FULL | "DEBIT E.F. MP.5-6 " | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 0 | 35 | CALCULTR | 30000.00 | 0.000000 | D0 | 30000.00 | 0.000000 | CLAMP | 0.000000 | [8 empty] | FI753C130.PV | -- | "----------------" | ONLYAUTO | 5000.000 | 25 | 3 |  |  | FI753A290.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1-(P2+P3) " | FI753B290.PV
10852 | LI004364() | HPM | FULL | "NIVEAU CLARIFICAT. " | "% " | " " | "DE " | " " | DE | 01 | 3 | 0 | 100 | DATAACQ | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER5.NN(1) | -- | "----------------" | ONLYAUTO | 98.00000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | 99.50000 | 94.00000 | -------- | -------- | LOW | ENABLE | [41 empty] | HIGH | CUTOUT | HIGH | CUTOUT | -------- | 92.00000 | NOACTION | CUTOUT | --------
10899 | LI005364() | HPM | FULL | "NIVEAU EAU CLARIFIEE " | "% " | " " | "DE " | " " | DE | 01 | 3 | 0 | 101 | DATAACQ | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER5.NN(2) | -- | "----------------" | ONLYAUTO | 98.00000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | 99.50000 | 86.00000 | -------- | -------- | LOW | ENABLE | [41 empty] | HIGH | CUTOUT | HIGH | CUTOUT | -------- | --------
10943 | FY020A324() | HPM | FULL | "CONVERT L/M_ML/MIN FFC08" | "ml / min" | " " | " " | " " | EA | 01 | 3 | 0 | 36 | CALCULTR | 28.33000 | 0.000000 | D2 | 34.00000 | -5.66000 | NOCLAMP | 0.000000 | [8 empty] | FI020324.PV | -- | "----------------" | ALL | -------- | 25 | 3 |  |  | FI020324.PVEUHI | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FFC080324.PVEUHI | [43 empty] | AUTO
10990 | FY020C324() | HPM | FULL | "CONVERT L/M_ML/MIN FFC08" | "ml / min" | " " | " " | " " | EA | 01 | 3 | 0 | 38 | CALCULTR | 28.33000 | 0.000000 | D2 | 34.00000 | -5.66000 | CLAMP | 0.000000 | [8 empty] | FI020324.PV | -- | "----------------" | ONLYAUTO | -------- | 25 | 3 |  |  | FI020324.PVEUHI | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FFC082324.PVEUHI
11036 | FI753100() | HPM | FULL | "DEBIT E.F COURS A BOIS" | "L/M " | " " | "DE " | " " | DE | 01 | 3 | 0 | 105 | DATAACQ | 10000.00 | 0.000000 | D0 | 12000.00 | -2000.00 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER2.NN(2) | -- | "----------------" | ONLYAUTO | 0.000000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
11074 | TI010364() | HPM | FULL | "TEMP. EAU CLARIFICAT. " | "degC " | " " | "DE " | " " | DE | 01 | 3 | 0 | 103 | DATAACQ | 50.00000 | 0.000000 | D1 | 60.00000 | -10.0000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER2.NN(1) | -- | "----------------" | ONLYAUTO | 22.00000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
11112 | LI017364() | HPM | FULL | "NIVEAU DU FLEUVE " | "metres " | " " | "DE " | " " | DE | 01 | 3 | 0 | 104 | CALCULTR | 11.30000 | 0.000000 | D2 | 12.50000 | -2.30000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER5.NN(7) | -- | "----------------" | ONLYAUTO | 9.680000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 100.0000 | 0.000000 | 0.000000 | 0.000000 | "P1/C1 "
11730 | FY044B311() | HPM | FULL | "TRIM O2 " | "M3/MIN " | " " | " " | " " | C1 | 01 | 3 | 0 | 97 | CALCULTR | 750.0000 | 0.000000 | D1 | 800.0000 | -100.000 | NOCLAMP | 0.000000 | [8 empty] | FY044C311.PVCALC | -- | "----------------" | ONLYAUTO | 400.0000 | 25 | 2 |  |  | AC080311.OP | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/(.8+(.004*P2)) "
12012 | PERTE_VAPEUR_310() | HPM | FULL | "PERTE VAPEUR SOUFFLANTE " | "Kg " | " " | " " | " " | AX | 01 | 3 | 0 | 115 | CALCULTR | 47500.00 | 0.000000 | D1 | 57000.00 | -9500.00 | NOCLAMP | 0.000000 | [8 empty] | PC311310.OP | -- | "----------------" | ONLYAUTO | 0.000000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*31800.0 "
12163 | SOMME_BOUE() | HPM | FULL | "SOMMATEUR DE BOUE " | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 0 | 106 | SUMMER | 1140.000 | 0.000000 | D1 | 1728.000 | -288.000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | BOUE_12_8.PV | -- | "----------------" | ONLYAUTO | 960.0000 | 25 | 3 |  |  | BOUE_8_4.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 1.000000 | 1.000000 | 1.000000 |  |  | BOUE_4_12.PV | [29 empty] | 0.000000
12210 | SOMME_HIER_BOUE() | HPM | FULL | "SOMMATEUR DE BOUE HIER" | "MINUTES " | " " | " " | " " | AX | 01 | 3 | 0 | 107 | SUMMER | 1440.000 | 0.000000 | D1 | 1728.000 | -288.000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | HIER_BOUE_12_8.PV | -- | "----------------" | ONLYAUTO | 960.0000 | 25 | 3 |  |  | HIER_BOUE_8_4.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 1.000000 | 1.000000 | 1.000000 |  |  | HIER_BOUE_4_12.PV | [29 empty] | 0.000000
12257 | TON_HIER_ECORCE() | HPM | FULL | "SOMMATEUR ECORCE HIER " | "tma " | " " | " " | " " | AX | 01 | 3 | 0 | 109 | SUMMER | 250.0000 | 0.000000 | D1 | 300.0000 | -50.0000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | HIER_ECORCE_12_8.PV | -- | "----------------" | ONLYAUTO | 210.0000 | 25 | 3 |  |  | HIER_ECORCE_8_4.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 1.000000 | 1.000000 | 1.000000 |  |  | HIER_ECORCE_4_12.PV | [29 empty] | 0.000000
12324 | TMA_HR_311() | HPM | FULL | "FORMULE BRULAGE ECORCES " | "tma/hre " | " " | " " | " " | AX | 01 | 3 | 0 | 110 | CALCULTR | 14.00000 | 0.000000 | D1 | 16.80000 | -2.80000 | NOCLAMP | 0.000000 | [8 empty] | FT003311.PV | -- | "----------------" | ONLYAUTO | 10.00000 | 25 | 3 |  |  | VAP_HUILE_311.PVTV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "((P1*0.0023)-(P2+P3))/11.11 " | VAP_GAZ_311.PV
12370 | VAP_HUILE_311() | HPM | FULL | "FORMULE VAPEUR VS HUILE " | "tma/hre " | " " | " " | " " | AX | 01 | 3 | 0 | 113 | CALCULTR | 63.65000 | 0.000000 | D1 | 76.38000 | -12.7300 | NOCLAMP | 0.000000 | [8 empty] | FT006311.PV | -- | "----------------" | ONLYAUTO | 0.000000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1*0.0156 "
12414 | VAP_GAZ_311() | HPM | FULL | "FORMULE VAPEUR VS GAZ " | "tma/hre " | " " | " " | " " | AX | 01 | 3 | 0 | 114 | CALCULTR | 80.98000 | 0.000000 | D1 | 97.18000 | -16.1900 | NOCLAMP | 0.000000 | [8 empty] | FT005311.PV | -- | "----------------" | ALL | -------- | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1*0.02183 " | [44 empty] | MAN
12459 | WQTMA311() | HPM | COMPONNT | "TONNAGE DES ECORCES " | "tma " | " " | " " | " " | AX | 01 | 3 | 0 | 111 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | TMA_HR_311.PVCALC
12488 | TONNE_ECORCE() | HPM | FULL | "SOMMATEUR ECORCE " | "tma " | " " | " " | " " | AX | 01 | 3 | 0 | 108 | SUMMER | 250.0000 | 0.000000 | D1 | 300.0000 | -50.0000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | ECORCE_12_8.PV | -- | "----------------" | ONLYAUTO | 210.0000 | 25 | 3 |  |  | ECORCE_8_4.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 1.000000 | 1.000000 | 1.000000 |  |  | ECORCE_4_12.PV | [29 empty] | 0.000000
12535 | COUT_PERTES_310() | HPM | FULL | "COUT PERTES VAPEUR SOUFF" | "DOLLARS " | " " | " " | " " | AX | 01 | 3 | 0 | 116 | CALCULTR | 680.0000 | 0.000000 | D2 | 816.0000 | -136.000 | NOCLAMP | 0.000000 | [8 empty] | PERTE_VAPEUR_310.PVCALC | -- | "----------------" | ONLYAUTO | 0.000000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/454.5*6.50 "
12579 | SOM_COUT_PERTES() | HPM | COMPONNT | "SOMME COUT PERTES VAPEUR" | "DOLLARS " | " " | " " | " " | AX | 01 | 3 | 0 | 117 | TOTALIZR | 1.000E08 | 0.000000 | D2 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | COUT_PERTES_310.PVCALC
12870 | FI008364() | HPM | FULL | "DEBIT D'ALUN " | "L/M " | " " | " " | " " | CE | 01 | 3 | 0 | 112 | CALCULTR | 14.20000 | 0.000000 | D1 | 16.80000 | -2.80000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_FISCHER1.NN(3) | -- | "----------------" | ONLYAUTO | 1.400000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | 0.200000 | -------- | -------- | NOACTION | ENABLE |  | 10.00000 | 0.000000 | 0.000000 | 0.000000 | "P1/C1 " | [37 empty] | HIGH | CUTOUT |  | --------
12949 | FQ003310() | HPM | COMPONNT | "DEBIT VAP. APPOINT REEL " | "Kg " | " " | " " | " " | DV | 01 | 3 | 0 | 49 | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI003310.PV
13040 | LY093311() | HPM | COMPONNT | "SOM. TRIM ALIM CHUTE " | "% " | " " | " " | " " | SE | 01 | 3 | 0 | 19 | CALCULTR | 100.0000 | 0.000000 | D1 | 115.0000 | -15.0000 | NOCLAMP | 0.000000 | [8 empty] | LC093311.OP | [5 empty] | 2 |  |  | SY094_095311.PVCALC | [13 empty] | 2.500000 | 20.00000 | 0.000000 | 0.000000 | "(P1/C1-C2)+P2 "
13576 | SY009311() | HPM | COMPONNT | "CONVERTION DE LY093311 " | "% " | " " | " " | " " | SE | 01 | 3 | 0 | 23 | CALCULTR | 18.00000 | 0.000000 | D1 | 19.00000 | -1.00000 | NOCLAMP | 0.000000 | [8 empty] | LC093311.OP | [5 empty] | 1 | [16 empty] | 5.550000 | 0.000000 | 0.000000 | 0.000000 | "P1/C1 "
14134 | SY094_095311() | HPM | COMPONNT | "SOMMATEUR CONV.ECORCES" | "% " | " " | "SE " | " " | SE | 01 | 3 | 0 | 24 | CALCULTR | 100.0000 | 0.000000 | D1 | 100.0000 | 0.000000 | NOCLAMP | 0.000000 | [8 empty] | HC094311.OP | [5 empty] | 4 |  |  | HC095311.OP | [13 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "(P1+P2+P3+P4)/4 " | HC096311.OP | [28 empty] | HC097311.OP
14296 | FY040A311() | HPM | FULL | "CARACTERISA. AIR/ECORCE" | "M3/MIN " | " " | " " | " " | C1 | 01 | 3 | 0 | 25 | GENLIN | 1600.000 | 0.000000 | D1 | 1800.000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | SY094_095311.PVCALC | -- | "----------------" | ONLYAUTO | 700.0000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 12 | 8.000000 | 500.0000 | 12.00000 | 518.5000 | 15.00000 | 536.2000 | 18.00000 | 544.2000 | 22.00000 | 562.4000 | 26.00000 | 580.5000 | 30.00000 | 599.0000 | 34.00000 | 617.0000 | 37.00000 | 635.0000 | 40.00000 | 653.0000 | [23 empty] | 42.00000 | 670.0000 | 45.00000 | 688.0000 | 50.00000 | 700.0000
14361 | FQ002_003366() | HPM | COMPONNT | "DEBIT DES BOUE " | "TONNES " | " " | "DV " | " " | DV | 01 | 3 | 0 | 92 | TOTALIZR | 1.000E08 | 0.000000 | D2 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQA | ANALOG | HOURS | 0.010000 | 0.000000 | -------- | -------- | -------- | NN_1_AXCH.NN(30)
14643 | FY450A311() | HPM | FULL | "CARACTERISA. AIR/ECORCE" | "M3/MIN " | " " | " " | " " | C1 | 01 | 3 | 0 | 32 | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | SY094_095311.PVCALC | -- | "----------------" | ONLYAUTO | 50.00000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 5 | 8.000000 | 56.00000 | 15.00000 | 58.00000 | 22.00000 | 60.00000 | 32.00000 | 65.00000 | 42.00000 | 69.00000 | 50.00000 | 72.00000
14772 | SOMME_T_BOUE_AUJ() | HPM | FULL | "SOMMATEUR DE BOUE TONN" | "TONNES " | " " | " " | " " | AX | 01 | 3 | 0 | 21 | SUMMER | 1140.000 | 0.000000 | D2 | 1728.000 | -288.000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | TONNES_BOUE_12_8.PV | -- | "----------------" | ONLYAUTO | 960.0000 | 25 | 3 |  |  | TONNES_BOUE_8_4.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 1.000000 | 1.000000 | 1.000000 |  |  | TONNES_BOUE_4_12.PV | [29 empty] | 0.000000
14819 | SOMME_T_BOUE_HIE() | HPM | FULL | "SOMMATEUR DE BOUE TONN" | "TONNES " | " " | " " | " " | AX | 01 | 3 | 0 | 22 | SUMMER | 1140.000 | 0.000000 | D2 | 1728.000 | -288.000 | NOCLAMP | 0.000000 | EQB |  |  | 1.000000 |  |  |  |  | HIER_T_BOUE_12_8.PV | -- | "----------------" | ONLYAUTO | 960.0000 | 25 | 3 |  |  | HIER_T_BOUE_8_4.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE |  | 1.000000 | 1.000000 | 1.000000 |  |  | HIER_T_BOUE_4_12.PV | [29 empty] | 0.000000
14866 | FI006321() | HPM | FULL | "DEBIT MAZOUTSTATION POMP" | "KG/H " | " " | " " | " " | MZ | 01 | 3 | 0 | 93 | CALCULTR | 10000.00 | 0.000000 | D0 | 12000.00 | -200.000 | NOCLAMP | 0.000000 | [8 empty] | NN_3_AXCH.NN(4) | -- | "----------------" | ONLYAUTO | 2000.000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | DISABLE |  | 4.354500 | 0.000000 | 0.000000 | 0.000000 | "P1*C1 "
14910 | TI006321() | HPM | FULL | "TEMP. MAZOUTSTATION POMP" | "DEG/C " | " " | " " | " " | MZ | 01 | 3 | 0 | 94 | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | NN_3_AXCH.NN(5) | -- | "----------------" | ONLYAUTO | 0.000000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | DISABLE |  | 0.011000 | 17.00000 | 0.000000 | 0.000000 | "P1*C1-C2 "
15042 | FY044C311() | HPM | FULL | "CARACTERISA. AIR/ECORCE" | "M3/MIN " | " " | " " | " " | C1 | 01 | 3 | 0 | 98 | GENLIN | 750.0000 | 0.000000 | D1 | 850.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | SY094_095311.PVCALC | -- | "----------------" | ONLYAUTO | 400.0000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 12 | 8.000000 | 110.0000 | 12.00000 | 123.0000 | 15.00000 | 136.0000 | 18.00000 | 149.0000 | 22.00000 | 162.0000 | 26.00000 | 175.0000 | 30.00000 | 188.0000 | 34.00000 | 200.0000 | 37.00000 | 213.0000 | 40.00000 | 226.0000 | [23 empty] | 42.00000 | 246.0000 | 45.00000 | 253.0000 | 50.00000 | 270.0000
15107 | TI200A109() | HPM | FULL | "PALIER ARR. DECHIQUETEUR" | "Deg C " | " " | "CR " | " " | CR | 01 | 3 | 0 | 28 | CALCULTR | 100.0000 | -100.000 | D1 | 115.0000 | -115.000 | NOCLAMP | 0.000000 | [8 empty] | NN_3_AXCH.NN(15) | -- | "----------------" | ONLYAUTO | 50.00000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | 70.00000 | 5.000000 | -------- | -------- | NOACTION | ENABLE |  | 10.00000 | 0.000000 | 0.000000 | 0.000000 | "P1/C1 " | [35 empty] | LOW | CUTOUT | HIGH | CUTOUT | 90.00000 | -------- |  |  | -------- | [7 empty] | LOW | CUTOUT
15160 | AY080A311() | HPM | FULL | "CARACTERISA. O2/ECORCE" | "%O2 " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 99 | GENLIN | 21.00000 | 0.000000 | D1 | 23.00000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | SY094_095311.PVCALC | -- | "----------------" | ONLYAUTO | 10.20000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 10 | 8.000000 | 11.50000 | 12.00000 | 11.35000 | 17.00000 | 11.20000 | 21.00000 | 11.05000 | 25.00000 | 10.90000 | 29.00000 | 10.75000 | 33.00000 | 10.60000 | 38.00000 | 10.45000 | 42.00000 | 10.30000 | 46.00000 | 10.15000 | [23 empty] | 100.0000 | 10.00000
15221 | TI200B109() | HPM | FULL | "PALIER AV. DECHIQUETEUR" | "Deg C " | " " | "CR " | " " | CR | 01 | 3 | 0 | 29 | CALCULTR | 100.0000 | -100.000 | D1 | 115.0000 | -115.000 | NOCLAMP | 0.000000 | [8 empty] | NN_3_AXCH.NN(16) | -- | "----------------" | ONLYAUTO | 50.00000 | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | 70.00000 | 5.000000 | -------- | -------- | NOACTION | ENABLE |  | 10.00000 | 0.000000 | 0.000000 | 0.000000 | "P1/C1 " | [35 empty] | LOW | CUTOUT | HIGH | CUTOUT | 90.00000 | -------- |  |  | -------- | [7 empty] | LOW | CUTOUT
15356 | FQ427500() | HPM | COMPONNT | "DEBIT VAPEUR 210KPA MP10" | "KG " | " " | "C6 " | " " | C6 | 01 | 3 | 0 | 26 | TOTALIZR | 1.000E08 | 0.000000 | D0 | 1.000E08 | 0.000000 | NOCLAMP | 0.000000 | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | -------- | FI427500.PV
15550 | AY088AA11() | HPM | FULL | "CARACTERISA. HUM/ECORCES" | "%HUM " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 118 | GENLIN | 100.0000 | 0.000000 | D1 | 115.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | AI088311.PVCALC | -- | "----------------" | ONLYAUTO | 45.00000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 10 | 0.000000 | 300.0000 | 20.00000 | 400.0000 | 30.00000 | 500.0000 | 40.00000 | 600.0000 | 50.00000 | 700.0000 | 60.00000 | 750.0000 | 70.00000 | 800.0000 | 80.00000 | 900.0000 | 90.00000 | 1000.000 | 95.00000 | 1050.000 | [23 empty] | 100.0000 | 1100.000
15663 | AY088B311() | HPM | FULL | "TRIM HUMIDIT " | "M3/MIN " | " " | " " | " " | C1 | 01 | 3 | 0 | 119 | CALCULTR | 1600.000 | -100.000 | D1 | 1800.000 | -200.000 | NOCLAMP | 0.000000 | [8 empty] | FY040A311.PVCALC | -- | "----------------" | ONLYAUTO | 700.0000 | 25 | 2 |  |  | HC088311.OP | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1+P2 "
15708 | AY088A311() | HPM | FULL | "CARACTERISA. HUM/ECORCES" | "%HUM " | " " | "C1 " | " " | C1 | 01 | 3 | 0 | 120 | GENLIN | 100.0000 | 0.000000 | D1 | 115.0000 | -20.0000 | NOCLAMP | 0.000000 | [8 empty] | AI088311.PVCALC | -- | "----------------" | ONLYAUTO | 45.00000 | 25 |  |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [7 empty] | 10 | 48.00000 | 0.000000 | 49.00000 | 5.000000 | 50.00000 | 10.00000 | 51.00000 | 15.00000 | 52.00000 | 20.00000 | 54.00000 | 25.00000 | 55.00000 | 30.00000 | 56.00000 | 35.00000 | 57.00000 | 40.00000 | 58.00000 | 45.00000 | [23 empty] | 60.00000 | 50.00000
16090 | LT101364() | HPM | FULL | "RESERVOIR BUSAN 1215 " | "% " | "BUSAN " | "1 " | " " | CE | 01 | 3 | 0 | 121 | CALCULTR | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_ASAE.NN(1) | -- | "LI101364 " | ONLYAUTO | -------- | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 4096.000 | 100.0000 | 0.000000 | 0.000000 | "p1/c1*c2 "
16134 | LT201364() | HPM | FULL | "HYPOCHLORITE DE SODIUM " | "% " | "NACLO " | " " | " " | CE | 01 | 3 | 0 | 122 | CALCULTR | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | 0.000000 | [8 empty] | NN_1_ASAE.NN(2) | -- | "----------------" | ONLYAUTO | -------- | 25 | 1 |  |  |  | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE |  | 4096.000 | 100.0000 | 0.000000 | 0.000000 | "P1/C1*C2 "