## HPM5 ANINNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PNTMODTY | SENSRTYP | PVCHAR | INPTDIR | PVEUHI | PVEULO | PVFORMAT | PVEXEUHI | PVEXEULO | PVCLAMP | LOCUTOFF | TF | PRIMMOD | PVSRCOPT | PVTV | OVERVAL | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | PVALDB | PVHITP | PVLOTP | PVLOPR | $LOSELCT | PVLLTP | PVROCPTP | PVROCNTP | BADPVPR | ALENBST | PVHIPR | $HISELCT | PVHHTP | PVLLPR | $LLSELCT
5449 | LT001316() | HPM | COMPONNT | "NIV.COND.CONTAMINE RICHE" | "% " | " " | " " | " " | C6 | 01 | 5 | 1 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000
5473 | LT008316() | HPM | COMPONNT | "NIV.EAU TRAITEE RECUP. " | "% " | " " | " " | " " | C6 | 01 | 5 | 1 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000
5497 | FI009316() | HPM | FULL | "DEBIT SORTIE EAU TRAITEE" | "L/M " | " " | " " | " " | C6 | 01 | 5 | 1 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 2300.000 | 0.000000 | D1 | 2760.000 | -460.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1100.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | 170.0000 | LOW | CUTOUT | -------- | -------- | -------- | LOW | DISABLE
5540 | AT012316() | HPM | COMPONNT | "CONDUCTIVITE REBOUILLEUR" | "uMHOS " | " " | " " | " " | C6 | 01 | 5 | 1 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 6000.000 | 0.000000 | D1 | 7200.000 | -1200.00 | NOCLAMP | -------- | 0.000000
5564 | PT027316() | HPM | COMPONNT | "PRESSION EAU VENTURIS " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 1 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 700.0000 | 0.000000 | D1 | 702.9000 | -2.90000 | NOCLAMP | -------- | 0.000000
5588 | PI028316() | HPM | FULL | "PRESSION VAPEUR PROPRE " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 1 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | 0.000000 | D1 | 402.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 210.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 275.0000 | 190.0000 | LOW | CUTOUT | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
5634 | TT038316() | HPM | COMPONNT | "TEMP.VAPEUR CONTAMINEE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 1 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000
5658 | FI044316() | HPM | FULL | "DEBIT VAPEUR PROPRE " | "KG/H " | " " | " " | " " | C6 | 01 | 5 | 1 | 8 | HLAI | 1_5_V | SQRROOT | DIRECT | 90718.00 | 0.000000 | D0 | 100000.0 | -13600.0 | CLAMP | 3400.000 | 0.100000 | -- | ONLYAUTO | 60000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 75000.00 | -------- |  |  |  | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
5701 | FT053316() | HPM | COMPONNT | "DEBIT GAZ INCONDENSABLES" | "KG/H " | " " | " " | " " | C6 | 01 | 5 | 1 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 2250.000 | 0.000000 | D1 | 2279.000 | -29.0000 | NOCLAMP | -------- | 0.000000
5725 | TI071316() | HPM | FULL | "TEMP.EAU SORTIE ECH.SPIR" | "DEGC " | " " | "C6 " | " " | C6 | 01 | 5 | 1 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 52.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
5765 | FI002316() | HPM | FULL | "DEBIT ECHANGEUR SPIRALE " | "L/M " | " " | " " | " " | C6 | 01 | 5 | 4 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 2000.000 | 0.000000 | D1 | 2500.000 | -600.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 1100.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
5805 | TI003316() | HPM | FULL | "TEMP.ENTREE EAU TRAITEE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 120.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
5845 | TI005316() | HPM | FULL | "TEMP.SORTIE EAU TRAITEE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 3 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 140.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
5885 | PI006316() | HPM | FULL | "PRES.SORTIE EAU TRAITEE " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 4 | 4 | HLAI | 1_5_V | LINEAR | DIRECT | 700.0000 | 0.000000 | D1 | 702.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 300.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
5925 | FI010316() | HPM | FULL | "DEBIT EAU TRAITEE " | "L/M " | " " | " " | " " | C6 | 01 | 5 | 4 | 5 | HLAI | 1_5_V | LINEAR | DIRECT | 37854.00 | 0.000000 | D1 | 40000.00 | -1000.00 | NOCLAMP | -------- | 0.350000 | -- | ONLYAUTO | 300.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 35000.00 | -------- |  |  |  | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | --------
5968 | LI013316() | HPM | FULL | "NIV.COND.CONTAM.PAUVRE " | "% " | " " | " " | " " | C6 | 01 | 5 | 4 | 6 | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 60.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | 40.00000 | NOACTION | CUTOUT | 1.000000 | -------- | -------- | LOW | ENABLE |  |  |  | NOACTION | CUTOUT
6013 | TI030316() | HPM | FULL | "TEMP. VAPEUR SALE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 7 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 145.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6053 | TI034316() | HPM | FULL | "TEMP. VAPEUR PROPRE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 8 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 140.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6093 | PI047140() | HPM | FULL | "PRESSION VAPEUR SALE " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 4 | 9 | HLAI | 1_5_V | LINEAR | DIRECT | 500.0000 | 0.000000 | D1 | 502.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 285.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6133 | PI050316() | HPM | FULL | "PRES. GAZ INCONDENSABLES" | "KPA " | " " | " " | " " | C6 | 01 | 5 | 4 | 10 | HLAI | 1_5_V | LINEAR | DIRECT | 700.0000 | 0.000000 | D1 | 702.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 272.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 325.0000 | 180.0000 | LOW | CUTOUT | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
6179 | TI051316() | HPM | FULL | "TEMP. GAZ INCONDENSABLES" | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 144.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6219 | FI074316() | HPM | FULL | "DEBIT EAU MACHINES " | "L/M " | " " | " " | " " | C6 | 01 | 5 | 4 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 3800.000 | 0.000000 | D1 | 4560.000 | -760.000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 3100.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | 750.0000 | LOW | CUTOUT | -------- | -------- | -------- | LOW | DISABLE
6262 | TI077316() | HPM | FULL | "TEMP. EAU RINCAGE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 35.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 90.00000 | -------- |  |  |  | -------- | -------- | LOW | DISABLE | LOW | CUTOUT | --------
6305 | TI082316() | HPM | FULL | "TEMP.SORTIE ECH.SPIRALE " | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 4 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 175.0000 | 0.000000 | D1 | 177.9000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 82.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6345 | PI083316() | HPM | FULL | "PRESSION CONDENSE EGOUT " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 4 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 210.0000 | 0.000000 | D1 | 252.0000 | -42.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 50.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | NOACTION | ENABLE
6385 | TI084316() | HPM | FULL | "TEMP.EAU ENTREE ECH.SPIR" | "DEGC " | " " | " " | " " | C6 | 01 | 5 | 5 | 1 | HLAI | 1_5_V | LINEAR | DIRECT | 65.00000 | 0.000000 | D1 | 67.90000 | -2.90000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 21.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6425 | PI079316() | HPM | FULL | "PRESSION EAU MACHINES " | "KpA " | " " | "C6 " | " " | C6 | 01 | 5 | 4 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 415.0000 | 0.000000 | D1 | 500.0000 | -85.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 210.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | 100.0000 | HIGH | CUTOUT | -------- | -------- | -------- | LOW | DISABLE
6654 | LT001314() | HPM | COMPONNT | "NIVEAU CHAUDIERE #4" | "mmH2O " | " " | "C4 " | " " | C4 | 01 | 5 | 1 | 11 | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | -400.000 | D1 | 480.0000 | -480.000 | NOCLAMP | -------- | 0.050000
6709 | JT007314() | HPM | COMPONNT | "PUISSANCE CHAUDIERE #4" | "MW " | " " | "C4 " | " " | C4 | 01 | 5 | 1 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 65.50000 | 0.100000 | D1 | 90.00000 | -12.0000 | NOCLAMP | -------- | 0.000000
6733 | AT008314() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #4 " | "uMHOS " | " " | "C4 " | " " | C4 | 01 | 5 | 1 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 5000.000 | 0.000000 | D1 | 6000.000 | -1000.00 | NOCLAMP | -------- | 0.000000
6757 | PT030314() | HPM | COMPONNT | "PRES. VAPEUR CHAUD. #4 " | "kPa " | " " | "C4 " | " " | C4 | 01 | 5 | 1 | 15 | HLAI | 1_5_V | LINEAR | DIRECT | 2070.000 | 0.000000 | D1 | 2484.000 | -414.000 | NOCLAMP | -------- | 0.000000
6853 | FI003314() | HPM | FULL | "DEBIT VAPEUR CHAUD. #4 " | "Kg/h " | " " | "C4 " | " " | C4 | 01 | 5 | 1 | 12 | HLAI | 1_5_V | LINEAR | DIRECT | 100000.0 | 0.000000 | D0 | 120000.0 | -20000.0 | NOCLAMP | 5000.000 | 0.000000 | -- | ONLYAUTO | 3000.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6893 | PI073B316() | HPM | FULL | "PRES. SORTIE ECHANGEUR " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 5 | 14 | HLAI | 1_5_V | LINEAR | DIRECT | 700.0000 | 0.000000 | D1 | 750.0000 | -50.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 280.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
6933 | PI073A316() | HPM | FULL | "PRES. ENTREE ECHANGEUR " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 5 | 13 | HLAI | 1_5_V | LINEAR | DIRECT | 700.0000 | 0.000000 | D1 | 750.0000 | -80.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 280.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- |  |  |  | -------- | -------- | LOW | ENABLE
7159 | JC613330() | HPM | COMPONNT | "CONSIGNE EXTERNE CH#4 " | "MW " | "MW USINE" | "C4 " | " " | C4 | 01 | 5 | 1 | 16 | HLAI | 1_5_V | LINEAR | DIRECT | 50.00000 | 0.000000 | D1 | 75.00000 | -20.0000 | NOCLAMP | -------- | 0.000000
7183 | JI613330() | HPM | FULL | "MEGAWATT USINE " | "MW " | " " | " " | " " | C4 | 01 | 5 | 5 | 2 | HLAI | 1_5_V | LINEAR | DIRECT | 250.0000 | 0.000000 | D1 | 300.0000 | -50.0000 | NOCLAMP | -------- | 0.000000 | -- | ONLYAUTO | 145.0000 | 25 | -- | NONE | NONE | 0 | 0 | HALF | 237.0000 | 100.0000 | LOW | CUTOUT | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------

## HPM5 ANOUTNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PNTMODTY | OPTDIR | OPCHAR | $OPTOL | OUTIND | $OLDEVDS | PRIMMOD | RCASOPT | NMODE | NMODATTR | MODEPERM | $MODESEL(1) | $MODESEL(3) | $MODESEL(5)
6468 | LV001A_B316() | HPM | COMPONNT | "NIV.COND.CONTANINE RICHE" | "% " | " " | " " | " " | C6 | 01 | 5 | 12 | 1 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6486 | LV008316() | HPM | COMPONNT | "NIV.EAU TRAITEE RECUP. " | "% " | " " | " " | " " | C6 | 01 | 5 | 12 | 2 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6504 | AV012316() | HPM | COMPONNT | "CONDUCTIVITE REBOUILLEUR" | "% " | " " | " " | " " | C6 | 01 | 5 | 12 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6522 | PV027A_B316() | HPM | COMPONNT | "PRESSION EAU VENTURIS " | "% " | " " | " " | " " | C6 | 01 | 5 | 12 | 4 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6540 | FV053316() | HPM | COMPONNT | "DEBIT GAZ INCONDENSABLES" | "% " | " " | " " | " " | C6 | 01 | 5 | 12 | 5 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6558 | HV024316() | HPM | FULL | "DILUTION CONDENSE " | "% " | " " | " " | " " | C6 | 01 | 5 | 20 | 2 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE | -- | NONE | MAN | NONE | PERMIT | ON | ON | ON
6781 | LV001314() | HPM | COMPONNT | "NIVEAU CHAUDIERE #4" | "% " | " " | "C4 " | " " | C4 | 01 | 5 | 12 | 7 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6799 | FV007314() | HPM | COMPONNT | "PUISSANCE CHAUDIERE #4" | "% " | " " | "C4 " | " " | C4 | 01 | 5 | 12 | 8 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6817 | AV008314() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #4 " | "% " | " " | "C4 " | " " | C4 | 01 | 5 | 12 | 9 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
6835 | PV030314() | HPM | COMPONNT | "PRES.VAPEUR CHAUDIERE #4" | "% " | " " | "C4 " | " " | C4 | 01 | 5 | 12 | 10 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE

## HPM5 ARRAY
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | EXTDATA | IOPNUM | FTANUM | DEVADDR | SCANPRI | AUXDATA1 | AB_DATA1 | AUXDATA2 | AB_DATA2 | AUXDATA3 | AB_DATA3 | AUXDATA4 | AB_DATA4 | FLSTIX | NFLAG | NNSTIX | NNUMERIC | STRSTIX | STRLEN | NSTRING | TIMESTIX | NTIME | SPLOCK | FLDESC | NNDESC | STRDESC | TIMEDESC | $ADD
83 | FL_1_ARV() | HPM | FULL | "COMM. 96 FLAG ARV " | "MODBUS " | " " | " " | C6 | 01 | 5 | 0 | 2 | -- | "----------------" | IO_FL | 14 | 2 | 116.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 5745 | 96 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ARV MODBUS 96 BIT A PARTIR DE 360-16 A 365-16 " | " " | " " | " " | ON
124 | NN_1_ARV() | HPM | FULL | "COMM. 5 REGISTRE ARVH " | "MODBUS " | " " | " " | C6 | 01 | 5 | 0 | 3 | -- | "----------------" | IO_NN | 14 | 2 | 116.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 40700 | 5 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COMM.PLC ARV MODBUS 5 REGISTRE A PARTIR DE 700 A 704 " | " " | " " | ON
2358 | FL_1_ACH4() | HPM | FULL | "COMM. 96 FLAG ACH4 " | "MODBUS " | " " | " " | C4 | 01 | 5 | 0 | 1 | -- | "----------------" | IO_FL | 14 | 1 | 101.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 5745 | 96 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ACH4 MODBUS 96 BIT A PARTIR DE 360-16 A 365-16 " | " " | " " | " " | ON
3281 | NN_1_ACH4() | HPM | FULL | "COMM. 6 REGISTRE ACH4 " | "MODBUS " | " " | " " | C4 | 01 | 5 | 0 | 4 | -- | "----------------" | IO_NN | 14 | 1 | 101.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 40700 | 6 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COMM.PLC ACH4 MODBUS 6 REGISTRE A PARTIR DE 700 A 705 " | " " | " " | ON

## HPM5 DIINNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | PNTMODTY | DITYPE | STATETXT(1) | STATETXT(0) | BOXCLR(1) | BOXCLR(0) | INPTDIR | PVSRCOPT | $AUXUNIT | $REALARM | ALMOPT | PVNORMAL | $DLYOPT | DLYTIME | OFFNRMPR | $OFSELCT | ALENBST | EVTOPT
6678 | CMOS_3() | HPM | FULL | "HPM3/4 CMOS BACKUP ALARM" | " " | " " | " " | " " | AX | 01 | 5 | 16 | 1 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
6973 | 4160V_69KV() | HPM | FULL | "FAUTE TERRE RESEAU 4160V" | " " | " " | " " | " " | AX | 01 | 5 | 17 | 2 | -- | DI | STATUS | "FAUTE " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7004 | 125VCC_DISJ() | HPM | FULL | "PERTE 125VCC DISJ. CH#4 " | " " | " " | " " | " " | AX | 01 | 5 | 17 | 5 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7035 | T5_TSH() | HPM | FULL | "TRANSFO T5S2 HI TEMP. " | " " | " " | " " | " " | AX | 01 | 5 | 17 | 3 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7066 | T5_TSHH() | HPM | FULL | "TRANSFO T5S2 HI-HI TEMP." | " " | " " | " " | " " | AX | 01 | 5 | 17 | 4 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7097 | JSH007314() | HPM | FULL | "HAUTE CHARGE CH#4 " | " " | " " | " " | " " | AX | 01 | 5 | 17 | 6 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7128 | 600V_69KV() | HPM | FULL | "FAUTE TERRE RESEAU 600V " | " " | " " | " " | " " | AX | 01 | 5 | 17 | 1 | -- | DI | STATUS | "FAUTE " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7229 | CMOS_5() | HPM | FULL | "HPM5/6 CMOS BACKUP ALARM" | " " | " " | " " | " " | AX | 01 | 5 | 16 | 4 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7260 | CMOS_7() | HPM | FULL | "HPM7/8 CMOS BACKUP ALARM" | " " | " " | " " | " " | AX | 01 | 5 | 16 | 7 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7291 | 24VDC_S3() | HPM | FULL | "HPM3/4 REDONDANT SUPPLY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 2 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7322 | 24VDC_S5() | HPM | FULL | "HPM5/6 REDONDANT SUPPLY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 5 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7353 | 24VDC_S7() | HPM | FULL | "HPM7/8 REDONDANT SUPPLY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 8 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7384 | 24VDC_P7() | HPM | FULL | "HPM7/8 PRIMAIRE SUPPLY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 9 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7415 | 24VDC_P5() | HPM | FULL | "HPM5/6 PRIMAIRE SUPPLY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 6 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7446 | 24VDC_P3() | HPM | FULL | "HPM3/4 PRIMAIRE SUPPLY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 3 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | EMERGNCY | CUTOUT | ENABLE | NONE
7477 | LO_PRIORITY() | HPM | FULL | "ALARMES DCS LO PRIORITY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 10 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | NOACTION | CUTOUT | ENABLE | NONE
7508 | HI_PRIORITY() | HPM | FULL | "ALARMES DCS HI PRIORITY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 11 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | NOACTION | CUTOUT | ENABLE | NONE
7539 | EMERGENCY() | HPM | FULL | "ALARMES DCS EMERGENCY " | " " | " " | " " | " " | AX | 01 | 5 | 16 | 12 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 0 | NOACTION | CUTOUT | ENABLE | NONE

## HPM5 FLAGNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | STATETXT(1) | STATETXT(0) | PV | BOXCLR(1) | BOXCLR(0) | $AUXUNIT | $REALARM | OFFNRMPR | $OFSELCT | ALENBST | EIPPCODE
1112 | A45_M4_316() | HPM | FULL | "POMPE RECIR. EAU CHAUDE " | "45_M4 " | "P.REC.EC" | " " | " " | C6 | 01 | 5 | 5 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1135 | A46_M4_316() | HPM | FULL | "POMPE SURPRES. E.CHAUDE " | "46-M4 " | "P.SUR.EC" | " " | " " | C6 | 01 | 5 | 6 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1158 | A47_M4_316() | HPM | FULL | "POMPE DILUTION VENTURIE " | "47-M4 " | "P.DIL.VE" | " " | " " | C6 | 01 | 5 | 7 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1181 | A49_M4_316() | HPM | FULL | "VENTILATEUR DE TOIT " | "49-M4 " | "VEN.TOIT" | " " | " " | C6 | 01 | 5 | 8 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1740 | FSL020316() | HPM | FULL | "BAS DEBIT VENTURIE #1 " | " " | "VENTUR.1" | " " | " " | C6 | 01 | 5 | 9 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1853 | FSL021316() | HPM | FULL | "BAS DEBIT VENTURIE #2 " | " " | "VENTUR.2" | " " | " " | C6 | 01 | 5 | 10 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1876 | FSL022316() | HPM | FULL | "BAS DEBIT VENTURIE #3 " | " " | "VENTUR.3" | " " | " " | C6 | 01 | 5 | 11 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
1899 | FSL023316() | HPM | FULL | "BAS DEBIT VENTURIE #4 " | " " | "VENTUR.4" | " " | " " | C6 | 01 | 5 | 12 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2203 | PSH920311() | HPM | FULL | "H.PRES.HYD.POUSSEUR ARR." | " " | " " | "LG " | " " | LG | 01 | 5 | 13 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2226 | PSH921311() | HPM | FULL | "H.PRES.HYD.POUSSEUR AVA." | " " | " " | "LG " | " " | LG | 01 | 5 | 14 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2249 | SSL922311() | HPM | FULL | "VIT.NULLE CONVOY. CENDRE" | " " | " " | "LG " | " " | LG | 01 | 5 | 15 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2773 | FSL020A314() | HPM | FULL | "E.GARN.POMPE RECIRCUL.A " | " " | "BAS DEB." | " " | " " | C4 | 01 | 5 | 16 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
2850 | LSH132109() | HPM | FULL | "CHUTE CONVOYEUR #38 " | " " | "H.NIV " | " " | " " | CR | 01 | 5 | 33 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2873 | LSL120109() | HPM | FULL | "HUILE UNITE HYD.CONV.#38" | " " | "B.NIV " | " " | " " | CR | 01 | 5 | 34 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2896 | SSL099109() | HPM | FULL | "DET. VITESSE CONV. #99 " | " " | "B.VIT. " | " " | " " | CR | 01 | 5 | 35 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2919 | YT16_W1_310() | HPM | FULL | "FAUTE ONDULEUR VENT.EVAC" | " " | "FT.ONDUL" | " " | " " | C1 | 01 | 5 | 3 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2942 | FSL020B314() | HPM | FULL | "E.GARN.POMPE RECIRCUL.B " | " " | "BAS DEB." | " " | " " | C4 | 01 | 5 | 17 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
2965 | FSL020C314() | HPM | FULL | "E.GARN.POMPE RECIRCUL.C " | " " | "BAS DEB." | " " | " " | C4 | 01 | 5 | 18 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
2988 | YT001314() | HPM | FULL | "CONTOURNE PROTEC.COL.EAU" | " " | "PROTECT." | " " | " " | C4 | 01 | 5 | 19 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3011 | LSHH011B314() | HPM | FULL | "COLONNE EAU CHAUDIERE #4" | " " | "T.H.NIV." | " " | " " | C4 | 01 | 5 | 20 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3034 | LSLL011A314() | HPM | FULL | "COLONNE EAU CHAUDIERE #4" | " " | "T.B.NIV." | " " | " " | C4 | 01 | 5 | 21 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3057 | PSHH030C314() | HPM | FULL | "VAPEUR CHAUDIERE #4 " | " " | "T.H.PRES" | " " | " " | C4 | 01 | 5 | 22 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3080 | PSLL030A314() | HPM | FULL | "VAPEUR CHAUDIERE #4 " | " " | "T.B.PRES" | " " | " " | C4 | 01 | 5 | 23 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3103 | PSL030B314() | HPM | FULL | "VAPEUR CHAUDIERE #4 " | " " | "BAS.PRES" | " " | " " | C4 | 01 | 5 | 24 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3126 | PSL499314() | HPM | FULL | "AIR INSTRUMENTATION " | " " | "BAS.PRES" | " " | " " | C4 | 01 | 5 | 25 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3149 | YT701314() | HPM | FULL | "RELAIS 86 DISJONCT.15-1 " | " " | "PROTECT." | " " | " " | C4 | 01 | 5 | 26 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3172 | URG_DISJ_C4() | HPM | FULL | "ARRET URG.DISJONCT.15-1 " | " " | "ARR.URG." | " " | " " | C4 | 01 | 5 | 27 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3492 | EV043143() | HPM | FULL | "VAPEUR TMP L3 FERMEE " | " " | "TMP L3 " | "C6 " | " " | C6 | 01 | 5 | 28 | -- | "FERMEE " | "OUVERTE " | FERMEE | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3515 | EV043144() | HPM | FULL | "VAPEUR TMP L4 FERMEE " | " " | "TMP L4 " | "C6 " | " " | C6 | 01 | 5 | 29 | -- | "FERMEE " | "OUVERTE " | FERMEE | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3538 | EV043145() | HPM | FULL | "VAPEUR TMP L5 FERMEE " | " " | "TMP L5 " | "C6 " | " " | C6 | 01 | 5 | 30 | -- | "FERMEE " | "OUVERTE " | FERMEE | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
3561 | SSL124109() | HPM | FULL | "DET. VITESSE CONV. #124 " | " " | "B.VIT. " | " " | " " | CR | 01 | 5 | 36 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3783 | SSL130109() | HPM | FULL | "DET. VITESSE CONV. #39 " | " " | "B.VIT. " | " " | " " | CR | 01 | 5 | 37 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3806 | SSL_37_M4() | HPM | FULL | "DET. VITESSE CONV. #100A" | " " | "B.VIT. " | " " | " " | CR | 01 | 5 | 38 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3829 | TSH121109() | HPM | FULL | "HUILE UNITE HYD.CONV.#38" | " " | "B.NIV. " | " " | " " | CR | 01 | 5 | 39 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3852 | ZS132A109() | HPM | FULL | "ALIGNEMENT CONVOYEUR #39" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 40 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3901 | ZS132B109() | HPM | FULL | "ALIGNEMENT CONVOYEUR #39" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 41 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3924 | ZS132C109() | HPM | FULL | "ALIGNEMENT CONVOYEUR #39" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 42 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
3947 | ZS132D109() | HPM | FULL | "ALIGNEMENT CONVOYEUR #39" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 43 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
4056 | ZS099109() | HPM | FULL | "CHUTE BLOQUEE CONV. #99 " | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 44 | -- | "ALARME " | "NORMAL " | ALARME | RED | GREEN | -- | 0 | HIGH | CUTOUT | DISABLE | --
4151 | ZS111109() | HPM | FULL | "CHUTE BLOQUEE DECHIQ-124" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 45 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
4174 | ZS124109() | HPM | FULL | "CHUTE BLOQUEE CONV. #124" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 46 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5353 | ALM_CONV_38() | HPM | FULL | "ARRET CONVOYEUR #38 " | " " | " " | " " | " " | CR | 01 | 5 | 47 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
5376 | F45_M4_316() | HPM | FULL | "POMPE RECIR. EN ARRET " | "45_M4 " | "P.REC.EC" | " " | " " | C6 | 01 | 5 | 4 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
5426 | LSHH111109() | HPM | FULL | "CHUTE BLOQUEE DECHIQ-124" | " " | "B.POS. " | " " | " " | CR | 01 | 5 | 48 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --

## HPM5 LOGICNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | USERID | LOGMIX | LISRC(1) | LISRC(2) | LISRC(3) | LISRC(4) | LISRC(5) | LISRC(6) | LISRC(7) | LISRC(8) | LISRC(9) | LISRC(10) | LISRC(11) | LISRC(12) | LIBADOPT | NN(001) | LOSRC(1) | LODSTN(1) | LOENBL(1) | LOSRC(2) | LODSTN(2) | LOENBL(2) | LOSRC(3) | LODSTN(3) | LOENBL(3) | LOSRC(4) | LODSTN(4) | LOENBL(4) | LOSRC(5) | LODSTN(5) | LOENBL(5) | LOSRC(6) | LODSTN(6) | LOENBL(6) | LOSRC(7) | LODSTN(7) | LOENBL(7) | LOSRC(8) | LODSTN(8) | LOENBL(8) | LOSRC(9) | LODSTN(9) | LOENBL(9) | LOSRC(10) | LODSTN(10) | LOENBL(10) | LOSRC(11) | LODSTN(11) | LOENBL(11) | LOSRC(12) | LODSTN(12) | LOENBL(12) | NODESC | $AUXUNIT | $REALARM | ALENBST | C1PR | C1DESC | C1SRC | C2PR | C2DESC | C2SRC | C3PR | C3DESC | C3SRC | C4PR | C4DESC | C4SRC | EIPPCODE | LOGALGID(1) | R1(1) | R2(1) | DEADBAND(1) | LOGALGID(2) | LOGALGID(3) | LOGALGID(4) | LOGALGID(5) | LOGALGID(6) | LOGALGID(7) | LOGALGID(8) | S1(1) | FL(0007) | NN(002) | S1REV(1) | S2(1) | S2REV(1) | S3(1) | S3REV(1)
1763 | FL5_1_VERS_ARV() | HPM | FULL | "TRANSFERT FLAG VERS PLC " | " " | " " | C6 | 01 | 5 | 1 | -- | "----------------" | 12_8_12 | LC008316.PVLLFL | FI010316.PVLOFL | PC027316.PVLOFL | PC027316.OP | FI074316.PVLOFL | PC079316.PVLOFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | 2.500000 NN(004)=60.00000 | L1 | LLL008316.SO | FL2 | L2 | FL010316.SO | FL2 | L3 | PL027316.SO | FL2 | SO1 | POH027316.SO | FL2 | L5 | FL074316.SO | FL2 | L6 | PL079316.SO | FL2 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | SO2 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | GT | L4 | NN4 | 5.000000 | NULL | NULL | NULL | NULL | NULL | NULL | NULL
1922 | ALARME5_1_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 5 | 2 | -- | "----------------" | 12_8_12 | --.-- | --.-- | --.-- | FL_1_ARV.FL(17) | FL_1_ARV.FL(16) | FL_1_ARV.FL(20) | FL_1_ARV.FL(24) | FL_1_ARV.FL(28) | FL_1_ARV.FL(56) | FL_1_ARV.FL(57) | FL_1_ARV.FL(58) | FL_1_ARV.FL(59) | HOLD |  | L1 | --.-- | FL1 | L2 | --.-- | FL1 | L3 | --.-- | FL1 | SO1 | F45_M4_316.PVFL | FL2 | L5 | A45_M4_316.PVFL | FL2 | L6 | A46_M4_316.PVFL | FL2 | L7 | A47_M4_316.PVFL | FL2 | L8 | A49_M4_316.PVFL | FL2 | L9 | FSL020316.PVFL | FL2 | L10 | FSL021316.PVFL | FL2 | L11 | FSL022316.PVFL | FL2 | L12 | FSL023316.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NOT |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL | L4
2009 | PATCHOUT5_1() | HPM | COMPONNT | "TRANSFERT OUTPUT " | " " | " " | AX | 01 | 5 | 3 |  |  | 12_8_12 | FY053316.PVCALC | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | 0.000000 | L1 | FV053316.OP | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | [17 empty] | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL |  | ON | 100.0000
2272 | ALARME5_2_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 5 | 4 | -- | "----------------" | 12_8_12 | --.-- | --.-- | --.-- | FL_1_ACH4.FL(62) | FL_1_ARV.FL(31) | FL_1_ARV.FL(36) | FL_1_ARV.FL(46) | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD |  | L1 | --.-- | FL1 | L2 | --.-- | FL1 | L3 | --.-- | FL1 | L4 | YT16_W1_310.PVFL | FL2 | L5 | EV043143.PVFL | FL2 | L6 | EV043144.PVFL | FL2 | L7 | EV043145.PVFL | FL2 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3195 | ALARME5_3_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 5 | 5 | -- | "----------------" | 12_8_12 | FL_1_ACH4.FL(49) | FL_1_ACH4.FL(50) | FL_1_ACH4.FL(51) | FL_1_ACH4.FL(52) | FL_1_ACH4.FL(54) | FL_1_ACH4.FL(55) | FL_1_ACH4.FL(56) | FL_1_ACH4.FL(57) | FL_1_ACH4.FL(58) | FL_1_ACH4.FL(59) | FL_1_ACH4.FL(60) | FL_1_ACH4.FL(61) | HOLD |  | L1 | FSL020A314.PVFL | FL2 | L2 | FSL020B314.PVFL | FL2 | L3 | FSL020C314.PVFL | FL2 | L4 | YT001314.PVFL | FL2 | L5 | LSHH011B314.PVFL | FL2 | L6 | LSLL011A314.PVFL | FL2 | L7 | PSHH030C314.PVFL | FL2 | L8 | PSLL030A314.PVFL | FL2 | L9 | PSL030B314.PVFL | FL2 | L10 | PSL499314.PVFL | FL2 | L11 | YT701314.PVFL | FL2 | L12 | URG_DISJ_C4.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3322 | ALARME5_4_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 5 | 6 | -- | "----------------" | 12_8_12 | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD |  | L1 | --.-- | FL1 | L2 | --.-- | FL1 | L3 | --.-- | FL1 | L4 | --.-- | FL1 | L5 | --.-- | FL1 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3584 | TRACKINGS_5_1() | HPM | FULL | "TRACKINGS DU HPM_5 " | " " | " " | AX | 01 | 5 | 7 | -- | "----------------" | 12_8_12 | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD |  | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 0 | -- | 0 | ENABLE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3670 | DIGITAL_5_OUTPUT() | HPM | FULL | "DO VERS EQUIPEMENTS " | " " | " " | AX | 01 | 5 | 8 | -- | "----------------" | 12_8_12 | EMERGENCY.PVFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD |  | L1 | ALARMES_DCS.SO | FL2 | L2 | --.-- | FL1 | L3 | --.-- | FL1 | L4 | --.-- | FL1 | L5 | --.-- | FL1 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | NOACTION | " " | NONE | -- | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3970 | ALARME_PLC_CR_1() | HPM | FULL | "ALARME PLC COUR VIA AXCH" | " " | " " | CR | 01 | 5 | 11 | -- | "----------------" | 12_8_12 | FL_1_AXCH.FL(171) | FL_1_AXCH.FL(172) | FL_1_AXCH.FL(173) | FL_1_AXCH.FL(174) | FL_1_AXCH.FL(175) | FL_1_AXCH.FL(176) | FL_1_AXCH.FL(177) | FL_1_AXCH.FL(178) | FL_1_AXCH.FL(179) | FL_1_AXCH.FL(180) | FL_1_AXCH.FL(181) | FL_1_AXCH.FL(184) | HOLD |  | L1 | LSH132109.PVFL | FL2 | L2 | LSL120109.PVFL | FL2 | L3 | SSL099109.PVFL | FL2 | L4 | SSL124109.PVFL | FL2 | L5 | SSL130109.PVFL | FL2 | L6 | SSL_37_M4.PVFL | FL2 | L7 | TSH121109.PVFL | FL2 | L8 | ZS132A109.PVFL | FL2 | L9 | ZS132B109.PVFL | FL2 | L10 | ZS132C109.PVFL | FL2 | L11 | ZS132D109.PVFL | FL2 | L12 | ZS099109.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL
4079 | XFERT_3_5_7_2() | HPM | COMPONNT | "TRANSFERT UNC 3 ET 7 A 5" | " " | " " | AX | 01 | 5 | 10 |  |  | 12_8_12 | HS005_006311.PVFL | HS005_006317.PVFL | HS005_006318.PVFL | FT006319.PV | WQTMA311.PV | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | 400.0000 | L1 | CALCUL_COUTS.FL(1) | FL2 | L2 | CALCUL_COUTS.FL(2) | FL2 | L3 | CALCUL_COUTS.FL(3) | FL2 | SO1 | CALCUL_COUTS.FL(4) | FL2 | L5 | CALCUL_COUTS.NN(13) | FL2 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | [17 empty] | GT | L4 | NN1 | 10.00000 | NULL | NULL | NULL | NULL | NULL | NULL | NULL |  | ON
4197 | ALARME_PLC_CR_2() | HPM | FULL | "ALARME PLC COUR VIA AXCH" | " " | " " | CR | 01 | 5 | 12 | -- | "----------------" | 12_8_12 | FL_1_AXCH.FL(185) | FL_1_AXCH.FL(186) | FL_1_AXCH.FL(147) | FL_1_AXCH.FL(161) | FL_1_AXCH.FL(208) | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD |  | L1 | ZS111109.PVFL | FL2 | L2 | ZS124109.PVFL | FL2 | SO1 | ALM_CONV_38.PVFL | FL2 | L4 | --.-- | FL1 | L5 | LSHH111109.PVFL | FL2 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | OR |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL | L3 |  |  | OFF | L4 | ON | FL1 | OFF
4289 | XFERT_3_5_7_1() | HPM | COMPONNT | "TRANSFERT UNC 3 ET 7 A 5" | " " | " " | AX | 01 | 5 | 9 |  |  | 12_8_12 | FQ006311.PV | FQ006317.PV | FQ006318.PV | FQ006319.PV | FQ050311.PV | FQ050317.PV | FQ050318.PV | FQ050319.PV | FQ003311.PV | FQ003317.PV | FQ003318.PV | FQ003319.PV | HOLD |  | L1 | CALCUL_COUTS.NN(1) | FL2 | L2 | CALCUL_COUTS.NN(2) | FL2 | L3 | CALCUL_COUTS.NN(3) | FL2 | L4 | CALCUL_COUTS.NN(4) | FL2 | L5 | CALCUL_COUTS.NN(5) | FL2 | L6 | CALCUL_COUTS.NN(6) | FL2 | L7 | CALCUL_COUTS.NN(7) | FL2 | L8 | CALCUL_COUTS.NN(8) | FL2 | L9 | CALCUL_COUTS.NN(9) | FL2 | L10 | CALCUL_COUTS.NN(10) | FL2 | L11 | CALCUL_COUTS.NN(11) | FL2 | L12 | CALCUL_COUTS.NN(12) | FL2 | [17 empty] | NULL |  |  |  | NULL | NULL | NULL | NULL | NULL | NULL | NULL |  | ON

## HPM5 NUMERNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PV | PVFORMAT
2137 | HIER_FQ009316() | HPM | COMPONNT | "INTEGRATION D'HIER " | "LITRE " | " " | " " | " " | C6 | 01 | 5 | 1 | 884606.0 | D1
2150 | HIER_FQ044316() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | " " | " " | C6 | 01 | 5 | 2 | 282565.0 | D1
2796 | CH4_POMPE_SEQ() | HPM | COMPONNT | "SEQUENCE POMPES A-B-C " | " " | " " | " " | " " | C4 | 01 | 5 | 6 | 4.000000 | D0
3437 | HIER_FQ003314() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C4 " | " " | C4 | 01 | 5 | 3 | 138752.0 | D1
3479 | HIER_JQ007314() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C4 " | " " | C4 | 01 | 5 | 4 | 179.6170 | D1
4388 | FQ006TOT() | HPM | COMPONNT | "INTEGRATION TOTAL MAZOUT" | "KG " | " " | " " | " " | MZ | 01 | 5 | 17 | 0.000000 | D1
4401 | FQ006TOT_NUIT() | HPM | COMPONNT | "INT. TOTAL MAZOUT NUIT " | "KG " | " " | " " | " " | MZ | 01 | 5 | 18 | 0.000000 | D1
4414 | FQ006TOT_JOUR() | HPM | COMPONNT | "INT. TOTAL MAZOUT JOUR " | "KG " | " " | " " | " " | MZ | 01 | 5 | 19 | 0.000000 | D1
4427 | FQ006TOT_SOIR() | HPM | COMPONNT | "INT. TOTAL MAZOUT SOIR " | "KG " | " " | " " | " " | MZ | 01 | 5 | 20 | 0.000000 | D1
4440 | FQ050TOT() | HPM | COMPONNT | "INTEGRATION TOTAL GAZ " | "M3 " | " " | " " | " " | GN | 01 | 5 | 21 | 0.000000 | D1
4453 | FQ050TOT_NUIT() | HPM | COMPONNT | "INT. TOTAL GAZ NUIT " | "M3 " | " " | " " | " " | GN | 01 | 5 | 22 | 0.000000 | D1
4466 | FQ050TOT_JOUR() | HPM | COMPONNT | "INT. TOTAL GAZ JOUR " | "M3 " | " " | " " | " " | GN | 01 | 5 | 23 | 0.000000 | D1
4479 | FQ050TOT_SOIR() | HPM | COMPONNT | "INT. TOTAL GAZ SOIR " | "M3 " | " " | " " | " " | GN | 01 | 5 | 24 | 0.000000 | D1
4492 | FQ003317MZ() | HPM | COMPONNT | "INT. VAPEUR PROD.MAZOUT " | "KG " | " " | " " | " " | MZ | 01 | 5 | 25 | 0.000000 | D1
4505 | FQ003317GN() | HPM | COMPONNT | "INT. VAPEUR PRODUIT GAZ " | "KG " | " " | " " | " " | GN | 01 | 5 | 26 | 455.4920 | D1
4518 | FQ003318GN() | HPM | COMPONNT | "INT. VAPEUR PRODUIT GAZ " | "KG " | " " | " " | " " | GN | 01 | 5 | 28 | 0.000000 | D1
4531 | FQ003319GN() | HPM | COMPONNT | "INT. VAPEUR PRODUIT GAZ " | "KG " | " " | " " | " " | GN | 01 | 5 | 30 | 0.000000 | D1
4544 | FQ003318MZ() | HPM | COMPONNT | "INT. VAPEUR PROD.MAZOUT " | "KG " | " " | " " | " " | MZ | 01 | 5 | 27 | 0.000000 | D1
4557 | FQ003319MZ() | HPM | COMPONNT | "INT. VAPEUR PROD.MAZOUT " | "KG " | " " | " " | " " | MZ | 01 | 5 | 29 | 0.000000 | D1
4570 | FQ003TOT_MZ() | HPM | COMPONNT | "INT. VAPEUR PROD. MAZOUT" | "KG " | " " | " " | " " | MZ | 01 | 5 | 31 | 0.000000 | D1
4583 | FQ003TOT_MZ_NUIT() | HPM | COMPONNT | "INT.VAP.PROD.MAZOUT NUIT" | "KG " | " " | " " | " " | MZ | 01 | 5 | 32 | 0.000000 | D1
4596 | FQ003TOT_MZ_JOUR() | HPM | COMPONNT | "INT.VAP.PROD.MAZOUT JOUR" | "KG " | " " | " " | " " | MZ | 01 | 5 | 33 | 0.000000 | D1
4609 | FQ003TOT_MZ_SOIR() | HPM | COMPONNT | "INT.VAP.PROD.MAZOUT SOIR" | "KG " | " " | " " | " " | MZ | 01 | 5 | 34 | 0.000000 | D1
4622 | FQ003TOT_GN() | HPM | COMPONNT | "INT. VAPEUR PRODUIT GAZ " | "KG " | " " | " " | " " | GN | 01 | 5 | 35 | 455.6710 | D1
4635 | FQ003TOT_GN_NUIT() | HPM | COMPONNT | "INT.VAP.PRODUIT GAZ NUIT" | "KG " | " " | " " | " " | GN | 01 | 5 | 36 | 249.4610 | D1
4648 | FQ003TOT_GN_JOUR() | HPM | COMPONNT | "INT.VAP.PRODUIT GAZ JOUR" | "KG " | " " | " " | " " | GN | 01 | 5 | 37 | 206.2640 | D1
4661 | FQ003TOT_GN_SOIR() | HPM | COMPONNT | "INT.VAP.PRODUIT GAZ SOIR" | "KG " | " " | " " | " " | GN | 01 | 5 | 38 | 0.000000 | D1
4703 | FQ003311MZ() | HPM | COMPONNT | "INT. VAPEUR PROD.MAZOUT " | "KG " | " " | " " | " " | MZ | 01 | 5 | 39 | 0.000000 | D1
4716 | FQ003311GN() | HPM | COMPONNT | "INT. VAPEUR PROD.MAZOUT " | "KG " | " " | " " | " " | GN | 01 | 5 | 40 | 0.000000 | D1
4729 | COUT_MZ_NUIT() | HPM | COMPONNT | "COUT MAZOUT QUART NUIT " | "$ " | " " | " " | " " | MZ | 01 | 5 | 41 | 0.000000 | D2
4742 | COUT_MZ_JOUR() | HPM | COMPONNT | "COUT MAZOUT QUART JOUR " | "$ " | " " | " " | " " | MZ | 01 | 5 | 42 | 0.000000 | D2
4755 | COUT_MZ_SOIR() | HPM | COMPONNT | "COUT MAZOUT QUART SOIR " | "$ " | " " | " " | " " | MZ | 01 | 5 | 43 | 0.000000 | D2
4768 | COUT_GN_SOIR() | HPM | COMPONNT | "COUT GAZ QUART SOIR " | "$ " | " " | " " | " " | GN | 01 | 5 | 46 | 0.000000 | D2
4781 | COUT_GN_JOUR() | HPM | COMPONNT | "COUT GAZ QUART JOUR " | "$ " | " " | " " | " " | GN | 01 | 5 | 45 | 0.000000 | D2
4794 | COUT_GN_NUIT() | HPM | COMPONNT | "COUT GAZ QUART NUIT " | "$ " | " " | " " | " " | GN | 01 | 5 | 44 | 0.000000 | D2
4807 | COUT_BM_NUIT() | HPM | COMPONNT | "COUT BIOMASSE QUART NUIT" | "$ " | " " | " " | " " | SE | 01 | 5 | 47 | 184.1580 | D2
4820 | COUT_BM_JOUR() | HPM | COMPONNT | "COUT BIOMASSE QUART JOUR" | "$ " | " " | " " | " " | SE | 01 | 5 | 48 | 2047.050 | D2
4833 | COUT_BM_SOIR() | HPM | COMPONNT | "COUT BIOMASSE QUART SOIR" | "$ " | " " | " " | " " | SE | 01 | 5 | 49 | 0.000000 | D2
4846 | COUT_EE_NUIT() | HPM | COMPONNT | "COUT ELECTRI. QUART NUIT" | "$ " | " " | " " | " " | C4 | 01 | 5 | 50 | 1651.060 | D2
4859 | COUT_EE_JOUR() | HPM | COMPONNT | "COUT ELECTRI. QUART JOUR" | "$ " | " " | " " | " " | C4 | 01 | 5 | 51 | 1340.460 | D2
4872 | COUT_EE_SOIR() | HPM | COMPONNT | "COUT ELECTRI. QUART SOIR" | "$ " | " " | " " | " " | C4 | 01 | 5 | 52 | 0.000000 | D2
4885 | COUT_VAP_MZ_NUIT() | HPM | COMPONNT | "COUT VAPEUR MAZOUT NUIT " | "$ " | " " | " " | " " | MZ | 01 | 5 | 53 | -------- | D2
4898 | COUT_VAP_MZ_JOUR() | HPM | COMPONNT | "COUT VAPEUR MAZOUT JOUR " | "$ " | " " | " " | " " | MZ | 01 | 5 | 54 | -------- | D2
4911 | COUT_VAP_MZ_SOIR() | HPM | COMPONNT | "COUT VAPEUR MAZOUT SOIR " | "$ " | " " | " " | " " | MZ | 01 | 5 | 55 | -------- | D2
4924 | COUT_VAP_GN_NUIT() | HPM | COMPONNT | "COUT VAPEUR GAZ NUIT " | "$ " | " " | " " | " " | GN | 01 | 5 | 56 | 0.000000 | D2
4937 | COUT_VAP_GN_JOUR() | HPM | COMPONNT | "COUT VAPEUR GAZ JOUR " | "$ " | " " | " " | " " | GN | 01 | 5 | 57 | 0.000000 | D2
4950 | COUT_VAP_GN_SOIR() | HPM | COMPONNT | "COUT VAPEUR GAZ SOIR " | "$ " | " " | " " | " " | GN | 01 | 5 | 58 | -------- | D2
4963 | COUT_VAP_BM_NUIT() | HPM | COMPONNT | "COUT VAPEUR BIOMASS.NUIT" | "$ " | " " | " " | " " | SE | 01 | 5 | 59 | 0.697018 | D2
4976 | COUT_VAP_BM_JOUR() | HPM | COMPONNT | "COUT VAPEUR BIOMASS.JOUR" | "$ " | " " | " " | " " | SE | 01 | 5 | 60 | 10.90320 | D2
4989 | COUT_VAP_BM_SOIR() | HPM | COMPONNT | "COUT VAPEUR BIOMASS.SOIR" | "$ " | " " | " " | " " | SE | 01 | 5 | 61 | -------- | D2
5002 | COUT_VAP_EE_NUIT() | HPM | COMPONNT | "COUT VAPEUR ELECTRI.NUIT" | "$ " | " " | " " | " " | C4 | 01 | 5 | 62 | 40.44170 | D2
5015 | COUT_VAP_EE_JOUR() | HPM | COMPONNT | "COUT VAPEUR ELECTRI.JOUR" | "$ " | " " | " " | " " | C4 | 01 | 5 | 63 | 33.04860 | D2
5028 | COUT_VAP_EE_SOIR() | HPM | COMPONNT | "COUT VAPEUR ELECTRI.SOIR" | "$ " | " " | " " | " " | C4 | 01 | 5 | 64 | -------- | D2
5041 | JQ007TOT_NUIT() | HPM | COMPONNT | "INT. TOTAL ELECT. NUIT " | "MW " | " " | " " | " " | C4 | 01 | 5 | 65 | 57.03150 | D1
5054 | JQ007TOT_JOUR() | HPM | COMPONNT | "INT. TOTAL ELECT. JOUR " | "MW " | " " | " " | " " | C4 | 01 | 5 | 66 | 46.34220 | D1
5067 | JQ007TOT_SOIR() | HPM | COMPONNT | "INT. TOTAL ELECT. SOIR " | "MW " | " " | " " | " " | C4 | 01 | 5 | 67 | 0.000000 | D1
5080 | WQTMATOT_NUIT() | HPM | COMPONNT | "INT. TOTAL BIOMASSE NUIT" | "TMA " | " " | " " | " " | SE | 01 | 5 | 68 | 3.497780 | D1
5093 | WQTMATOT_JOUR() | HPM | COMPONNT | "INT. TOTAL BIOMASSE JOUR" | "TMA " | " " | " " | " " | SE | 01 | 5 | 69 | 38.93820 | D1
5106 | WQTMATOT_SOIR() | HPM | COMPONNT | "INT. TOTAL BIOMASSE SOIR" | "TMA " | " " | " " | " " | SE | 01 | 5 | 70 | 0.000000 | D1
5119 | FQ003TOT_BM() | HPM | COMPONNT | "INT.VAP TOTAL A BIOMASSE" | "KG " | " " | " " | " " | SE | 01 | 5 | 71 | 452.2640 | D1
5132 | FQ003TOT_BM_NUIT() | HPM | COMPONNT | "INT.VAP TOT.BIOMASS.NUIT" | "KG " | " " | " " | " " | SE | 01 | 5 | 72 | 264.2080 | D1
5145 | FQ003TOT_BM_JOUR() | HPM | COMPONNT | "INT.VAP TOT.BIOMASS.JOUR" | "KG " | " " | " " | " " | SE | 01 | 5 | 73 | 188.0820 | D1
5158 | FQ003TOT_BM_SOIR() | HPM | COMPONNT | "INT.VAP TOT.BIOMASS.SOIR" | "KG " | " " | " " | " " | SE | 01 | 5 | 74 | 0.000000 | D1
5171 | FQ003TOT_EE_NUIT() | HPM | COMPONNT | "INT.VAP TOT.ELECTR. NUIT" | "KG " | " " | " " | " " | C4 | 01 | 5 | 75 | 40.82570 | D1
5184 | FQ003TOT_EE_JOUR() | HPM | COMPONNT | "INT.VAP TOT.ELECTR. JOUR" | "KG " | " " | " " | " " | C4 | 01 | 5 | 76 | 40.61520 | D1
5197 | FQ003TOT_EE_SOIR() | HPM | COMPONNT | "INT.VAP TOT.ELECTR. SOIR" | "KG " | " " | " " | " " | C4 | 01 | 5 | 77 | 0.000000 | D1
5210 | FQ044316_NUIT() | HPM | COMPONNT | "INT.VAP REBOUILLEUR NUIT" | "KG " | " " | " " | " " | C6 | 01 | 5 | 78 | 129.2590 | D1
5223 | FQ044316_JOUR() | HPM | COMPONNT | "INT.VAP REBOUILLEUR JOUR" | "KG " | " " | " " | " " | C6 | 01 | 5 | 79 | 38.81380 | D1
5236 | FQ044316_SOIR() | HPM | COMPONNT | "INT.VAP REBOUILLEUR SOIR" | "KG " | " " | " " | " " | C6 | 01 | 5 | 80 | 0.000000 | D1
5249 | FQ003_NUIT() | HPM | COMPONNT | "PRODUCTION VAPEUR NUIT " | "KG " | " " | " " | " " | AX | 01 | 5 | 81 | 683.7540 | D1
5262 | FQ003_JOUR() | HPM | COMPONNT | "PRODUCTION VAPEUR JOUR " | "KG " | " " | " " | " " | AX | 01 | 5 | 82 | 474.9200 | D1
5275 | FQ003_SOIR() | HPM | COMPONNT | "PRODUCTION VAPEUR SOIR " | "KG " | " " | " " | " " | AX | 01 | 5 | 83 | 0.000000 | D1
5288 | COUT_NUIT() | HPM | COMPONNT | "COUT CONBUSTIBLE NUIT " | "$ " | " " | " " | " " | AX | 01 | 5 | 84 | 1835.220 | D1
5301 | COUT_JOUR() | HPM | COMPONNT | "COUT CONBUSTIBLE JOUR " | "$ " | " " | " " | " " | AX | 01 | 5 | 85 | 3395.530 | D1
5314 | COUT_SOIR() | HPM | COMPONNT | "COUT CONBUSTIBLE SOIR " | "$ " | " " | " " | " " | AX | 01 | 5 | 86 | 0.000000 | D1
5327 | COUT_JOURNEE() | HPM | COMPONNT | "COUT CONBUSTIBLE JOURNEE" | "$ " | " " | " " | " " | AX | 01 | 5 | 87 | 5231.300 | D1
5340 | FQ003_JOURNEE() | HPM | COMPONNT | "VAPEUR PRODUITE JOURNEE " | "$ " | " " | " " | " " | AX | 01 | 5 | 88 | 1158.900 | D1

## HPM5 PRMODNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | USERID | STRLEN | SEQSLTSZ | CNTLLOCK | SPLOCK | RSTROPT | ACP | CLBACK | SEQPR | TIME(001) | NN(001) | FL(0001) | NN(005) | NN(009) | NN(013) | NN(023) | NN(027) | NN(031) | NN(035) | NN(039) | NN(043) | FL(0014)
2163 | INTEGRE5_1() | HPM | FULL | "TRANSFERT INTEGRE.MINUIT" | "INTEGRE " | " " | AX | 01 | 5 | 1 | -- | "----------------" | 8 | 10 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-13:41:36" TIME(002)="08/20/01 15:18:46"
2183 | HPM5_PLC_1() | HPM | FULL | "TRANSFERT VERS LES PLC " | " " | " " | AX | 01 | 5 | 2 | -- | "----------------" | 8 | 20 | OPERATOR | OPERATOR | OFF | -- | 0 | NOACTION |  | 2.500000
2809 | CH4_AUTO_CAS() | HPM | FULL | "FORCE MODE CAS JC007314 " | "C4 " | " " | C4 | 01 | 5 | 3 | -- | "----------------" | 8 | 10 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-14:51:33" TIME(002)="08/20/01 15:18:46"
2829 | CH4_POMPES() | HPM | FULL | "DEPART POMPE AUTOMATIQUE" | "C4 " | " " | C4 | 01 | 5 | 4 | -- | "----------------" | 8 | 20 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-14:51:33" TIME(002)="08/20/01 15:18:46" |  | ON FL(0002)=ON FL(0003)=ON FL(0004)=ON FL(0005)=ON
4357 | CALCUL_COUTS() | HPM | FULL | "TABLEAU CALCUL DES COUTS" | "COUTS " | " " | AX | 01 | 5 | 6 | -- | "----------------" | 8 | 50 | ENGINEER | SUPERVIS | OFF | -- | 0 | NOACTION | " 0-13:45:08" TIME(002)="08/20/01 15:18:46" | 0.000000 NN(002)=0.000000 NN(003)=0.000000 NN(004)=0.000000 |  | 0.000000 NN(006)=0.000000 NN(007)=0.000000 NN(008)=0.000000 | 451574.0 NN(010)=455260.0 NN(011)=0.000000 NN(012)=0.000000 | 42.29910 NN(020)=0.369600 NN(021)=0.303900 NN(022)=28.95000 | 52.65000 NN(024)=23.32920 NN(025)=22.06470 NN(026)=18.68720 | 7.265700 NN(028)=0.000000 NN(029)=0.000000 NN(030)=0.000000 | 0.000000 NN(032)=1800.300 NN(033)=197.1940 NN(034)=1997.490 | 0.000000 NN(036)=0.000000 NN(037)=1736.990 NN(038)=-46.3166 | 1690.670 NN(040)=0.000000 NN(041)=0.000000 NN(042)=1662.130 | 10.40360 NN(044)=1672.530 NN(045)=5360.700 NN(046)=0.000000 | ON

## HPM5 REGCLNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | CTLALGID | PVEUHI | PVEULO | PVFORMAT | PVSRCOPT | OVERVAL | BADCTLOP | RCASOPT | NMODE | NMODATTR | MODEPERM | $MODESEL(1) | $MODESEL(5) | $MODESEL(2) | $MODESEL(3) | $MODESEL(4) | $BADOCMD | EXTSWOPT | SPHILM | SPLOLM | $SPTOL | SP | SPOPT | RBOPT | PIDFORM | CTLEQN | PVTRACK | CTLACTN | GAINOPT | K | T1 | T2 | NOCINPTS | CISRC(1) | NOCOPTS | CODSTN(1) | OUTIND | OPHILM | OPLOLM | SAFEOP | OPMCHLM | OPROCLM | $OPTOL | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | BADOCOPT | OPALDB | OPHITP | OPLOTP | PVALDB | PVHITP | PVHIPR | $HISELCT | PVLOTP | PVLOPR | $LOSELCT | PVHHTP | PVLLTP | PVROCPTP | PVROCNTP | BADPVPR | DEVHITP | DEVLOTP | ALENBST | PVLLPR | $LLSELCT | PVSGCHTP | CVEUHI | CVEULO | CISRC(2) | B | RATE1 | XEUHI | XEULO | BADCTLPR
2 | LC001316() | HPM | FULL | "NIV.COND.CONTAMINE RICHE" | "% " | " " | " " | " " | C6 | 01 | 5 | 0 | 21 | -- | "----------------" | PID | 100.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 100.0000 | 0.000000 | 0.000000 | 60.00000 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 2.000000 | 4.050000 | 0.000000 | 1 | LT001316.PV | 1 | LV001A_B316.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 90.00000 | LOW | CUTOUT | 30.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
165 | LC008316() | HPM | FULL | "NIV. EAU TRAITEE RECUP. " | "% " | " " | " " | " " | C6 | 01 | 5 | 0 | 22 | -- | "----------------" | PID | 100.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | NONE |  | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 100.0000 | 0.000000 | 0.000000 | 70.03890 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 1.400000 | 3.000000 | 0.000000 | 1 | LT008316.PV | 1 | LV008316.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 95.00000 | LOW | CUTOUT | 50.00000 | EMERGNCY | CUTOUT | -------- | 35.00000 | -------- | -------- | LOW | -------- | -------- | ENABLE | EMERGNCY | CUTOUT | --------
248 | AC012316() | HPM | FULL | "CONDUCTIVITE REBOUILLEUR" | "uMHOS " | "% " | "C6 " | " " | C6 | 01 | 5 | 0 | 23 | -- | "----------------" | PID | 6000.000 | 0.000000 | D0 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 6000.000 | 0.000000 | 0.000000 | 3200.000 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 5.000000 | 10.00000 | 0.000000 | 1 | AT012316.PV | 1 | AV012316.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 3900.000 | LOW | CUTOUT | 2500.000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
329 | PC027316() | HPM | FULL | "PRESSION EAU VENTURIS " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 0 | 24 | -- | "----------------" | PID | 700.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 700.0000 | 0.000000 | 0.000000 | 520.2450 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 2.200000 | 0.300000 | 0.000000 | 1 | PT027316.PV | 1 | PV027A_B316.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 700.0000 | LOW | CUTOUT | 140.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
454 | TC038316() | HPM | FULL | "TEMP. VAPEUR CONTAMINEE " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 0 | 25 | -- | "----------------" | PID | 175.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 175.0000 | 0.000000 | 0.000000 | 136.0290 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 2.000000 | 0.500000 | 0.000000 | 1 | TT038316.PV | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 150.0000 | LOW | CUTOUT | 120.0000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | 100.0000 | 0.000000
536 | FC053316() | HPM | FULL | "DEBIT GAZ INCONDENSABLES" | "KG/H " | " " | " " | " " | C6 | 01 | 5 | 0 | 26 | -- | "----------------" | PID | 2250.000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 2250.000 | 0.000000 | 0.000000 | 0.000000 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 1.000000 | 0.100000 | 0.000000 | 1 | FT053316.PV | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 1360.000 | LOW | CUTOUT | -------- |  |  | -------- |  | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | 100.0000 | 0.000000
615 | PC079316() | HPM | FULL | "PRESSION EAU MACHINES " | "KPA " | " " | " " | " " | C6 | 01 | 5 | 0 | 28 | -- | "----------------" | PID | 415.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 415.0000 | 0.000000 | 0.000000 | 168.0000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | DIRECT | LIN | 2.000000 | 0.700000 | 0.000000 | 1 | PI079316.PV | 1 | " " | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 350.0000 | LOW | CUTOUT | 15.00000 | LOW | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
2399 | LC001314() | HPM | FULL | "NIVEAU CHAUDIERE #4" | "mmH2O " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 1 | -- | "----------------" | PID | 400.0000 | -400.000 | D0 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 400.0000 | -400.000 | 0.000000 | -50.0000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 3.000000 | 1.000000 | 0.000000 | 1 | LT001314.PV | 1 | LV001314.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 375.0000 | HIGH | CUTOUT | -250.000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
2480 | JC007314() | HPM | FULL | "PUISSANCE CHAUDIERE #4" | "MW " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 2 | -- | "----------------" | PID | 65.50000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 50.00000 | 0.000000 | 0.000000 | 7.499980 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.700000 | 0.075000 | 0.000000 | 2 | JT007314.PV | 1 | FV007314.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 53.00000 | HIGH | CUTOUT | -------- |  |  | -------- |  | -------- | -------- | LOW | -------- | -------- | ENABLE | [5 empty] | JY007B314.PV
2559 | AC008314() | HPM | FULL | "CONDUCTIVITE CHAUD. #4 " | "uMHOS " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 3 | -- | "----------------" | PID | 5000.000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 5000.000 | 0.000000 | 0.000000 | 2000.000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | DIRECT | LIN | 10.00000 | 5.000000 | 0.000000 | 1 | AT008314.PV | 1 | AV008314.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 2400.000 | HIGH | CUTOUT | 1000.000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
2640 | PC030314() | HPM | FULL | "PRES.VAPEUR CHAUDIERE #4" | "kPa " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 4 | -- | "----------------" | PID | 2070.000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 2070.000 | 0.000000 | 0.000000 | 800.0000 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 5.000000 | 0.750000 | 0.000000 | 1 | PT030314.PV | 1 | PV030314.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 1550.000 | HIGH | CUTOUT | 480.0000 | HIGH | CUTOUT | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
2721 | HC310314() | HPM | FULL | "MAITRE CHAUDIERE #4" | "% " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 29 | -- | "----------------" | AUTOMAN |  |  |  |  | 25 | NO_SHED | NONE | MAN | NONE | PERMIT | ON | ON |  | ON | ON | SHEDMAN | NONE | [7 empty] | EQA | [6 empty] | 1 | PC310310.OP | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- |  | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | [14 empty] | ENABLE | [6 empty] | -20.0000 | 0.000000 | 100.0000 | 0.000000 | LOW

## HPM5 REGPVNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | PVALGID | PVEUHI | PVEULO | PVFORMAT | PVEXEUHI | PVEXEULO | PVCLAMP | PVSRCOPT | TF | PVTV | OVERVAL | PVEQN | N | NMIN | FRCPERM | PISRC(1) | PISRC(2) | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | PVALDB | PVHITP | PVLOTP | PVROCPTP | PVROCNTP | BADPVPR | ALENBST | DEVHITP | ACCTYPE | TIMEBASE | C | RESETVAL | CUTOFFLM | AVTV | AVDEV1TP | C1 | C2 | C3 | C4 | CALCEXP
410 | FY053316() | HPM | FULL | "HI SELECTEUR TC038-FC053" | " " | " " | " " | " " | C6 | 01 | 5 | 0 | 21 | -- | "----------------" | HILOAVG | 100.0000 | 0.000000 | D1 | 102.9000 | -2.90000 | NOCLAMP | ONLYAUTO | 0.000000 | 14.00000 | 25 | EQA | 2 | 2 | OFF | TC038316.OP | FC053316.OP | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | --------
2079 | FQ009316() | HPM | COMPONNT | "DEBIT SORTIE EAU TRAITEE" | "LITRE " | " " | " " | " " | C6 | 01 | 5 | 0 | 33 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 |  |  | EQB |  |  |  | FI009316.PV | [14 empty] | ANALOG | MINUTES | 1.000000 | 0.000000 | 0.000000 | -------- | --------
2108 | FQ044316() | HPM | COMPONNT | "DEBIT VAPEUR PROPRE " | "KG " | " " | " " | " " | C6 | 01 | 5 | 0 | 34 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 |  |  | EQB |  |  |  | FI044316.PV | [14 empty] | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
3408 | FQ003314() | HPM | COMPONNT | "DEBIT VAPEUR CHAUDIERE#4" | "KG " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 35 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 |  |  | EQB |  |  |  | FI003314.PV | [14 empty] | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
3450 | JQ007314() | HPM | COMPONNT | "PUISSANCE CHAUDIERE#4 " | "MW " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 36 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 |  |  | EQB |  |  |  | JT007314.PV | [14 empty] | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
3756 | JY007A314() | HPM | COMPONNT | "CONVERTIR % EN MW " | "MW " | " " | " " | " " | C4 | 01 | 5 | 0 | 1 |  |  | CALCULTR | 50.00000 | 0.000000 | D1 | 65.00000 | -0.50000 | NOCLAMP |  | 0.000000 |  |  |  | 1 |  |  | HC310314.OP | [21 empty] | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1*0.5 "
3875 | JY007B314() | HPM | COMPONNT | "LO SELECT MAITRE - RSP" | "MW " | " " | " " | " " | C4 | 01 | 5 | 0 | 2 |  |  | HILOAVG | 50.00000 | 0.000000 | D1 | 63.00000 | -3.00000 | NOCLAMP |  | 0.330000 |  |  | EQB | 2 | 2 | OFF | JC613330.PV | JY007A314.PVCALC
4674 | JQ613330() | HPM | COMPONNT | "PUISSANCE DISPONIBLE C#4" | "MW " | " " | "C4 " | " " | C4 | 01 | 5 | 0 | 37 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 |  |  | EQB |  |  |  | JC613330.PV | [14 empty] | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
5399 | FY009316() | HPM | COMPONNT | "DEBIT VAPEUR CALCULE C6 " | "KG/H " | " " | "C6 " | " " | C6 | 01 | 5 | 0 | 22 |  |  | CALCULTR | 90718.00 | 0.000000 | D0 | 100000.0 | -0.50000 | NOCLAMP |  | 0.000000 |  |  |  | 1 |  |  | FI009316.PV | [21 empty] | 54.13000 | 0.000000 | 0.000000 | 0.000000 | "P1*C1 "