## HPM7 ANINNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | PNTMODTY | SENSRTYP | PVCHAR | INPTDIR | PVEUHI | PVEULO | PVFORMAT | PVEXEUHI | PVEXEULO | PVCLAMP | LOCUTOFF | PVSRCOPT | TF | PVTV | OVERVAL | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | PVALDB | PVHITP | PVLOTP | PVROCPTP | PVROCNTP | BADPVPR | ALENBST | PVHIPR | $HISELCT | PVHHTP | PVHHPR | $HHSELCT | PVLOPR | $LOSELCT | PVLLTP
6182 | PI041318() | HPM | FULL | "PRESSION AIR AU BRULEUR " | "mmH2O " | " " | "C8 " | " " | C8 | 01 | 7 | 4 | 8 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1270.000 | 0.000000 | D0 | 1524.000 | -254.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1400.000 | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- | -------- | -------- | -------- | LOW | ENABLE
6222 | PI042318() | HPM | FULL | "PRESSION DU FOYER CH#8 " | "mmH2O " | " " | "C8 " | " " | C8 | 01 | 7 | 4 | 16 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1270.000 | 0.000000 | D0 | 1524.000 | -254.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1400.000 | 25 | -- | NONE | NONE | 0 | 0 | FIVE | -------- | -------- | -------- | -------- | LOW | ENABLE
6262 | TI800318() | HPM | FULL | "TEMP.AIR AU BRULEUR " | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 1 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 58.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6302 | FT003317() | HPM | FULL | "DEBIT VAPEUR CHAUD. #7 " | "Kg/h " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 3 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 136000.0 | 0.000000 | D0 | 163200.0 | -27200.0 | NOCLAMP | 6800.000 | ONLYAUTO | 0.000000 | 75000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6342 | FT003318() | HPM | FULL | "DEBIT VAPEUR CHAUD. #8 " | "Kg/h " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 10 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 90720.00 | 0.000000 | D0 | 120000.0 | -20000.0 | NOCLAMP | 4500.000 | ONLYAUTO | 0.000000 | 75000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6382 | FT003319() | HPM | FULL | "DEBIT VAPEUR CHAUD. #9 " | "Kg/h " | " " | "C9 " | " " | C9 | 01 | 7 | 1 | 2 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 64000.00 | 0.000000 | D0 | 76800.00 | -12800.0 | NOCLAMP | 3200.000 | ONLYAUTO | 0.000000 | 40000.00 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6422 | FT006317() | HPM | FULL | "DEBIT MAZOUT CHAUD. #7 " | "Kg/h " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 9 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 10000.00 | 0.000000 | D1 | 12000.00 | -2000.00 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6462 | FT006318() | HPM | FULL | "DEBIT MAZOUT CHAUD. #8 " | "Kg/h " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 13 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 7130.000 | 0.000000 | D1 | 8556.000 | -1426.00 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 7100.000 | -------- | -------- | -------- | LOW | ENABLE | LOW | CUTOUT | --------
6505 | FT006319() | HPM | FULL | "DEBIT MAZOUT CHAUD. #9 " | "Kg/h " | " " | "C9 " | " " | C9 | 01 | 7 | 1 | 5 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 3045.830 | 0.000000 | D1 | 3654.000 | -609.000 | NOCLAMP | 500.0000 | ONLYAUTO | 0.000000 | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | NOACTION | ENABLE
6545 | DI084318() | HPM | FULL | "DENSITE MAZOUT CH#8 " | "g/cc " | " " | "C8 " | " " | C8 | 01 | 7 | 4 | 15 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1.250000 | 0.750000 | D2 | 1.350000 | 0.650000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6585 | TI804318() | HPM | FULL | "TEMP.MAZOUT CHAUDIERE #8" | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 5 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 150.0000 | 0.000000 | D1 | 180.0000 | -30.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6625 | LT001317() | HPM | FULL | "NIVEAU CHAUDIERE #7" | "mmH2O " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 1 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | -400.000 | D1 | 480.0000 | -480.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6665 | FT002317() | HPM | FULL | "DEBIT EAU CHAUDIERE #7" | "Kg/h " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 2 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 163300.0 | 0.000000 | D0 | 19596000 | -32660.0 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6705 | FT004A317() | HPM | FULL | "DEBIT AIR BRULEUR #1 " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 4 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -25.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 50.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6745 | FT004B317() | HPM | FULL | "DEBIT AIR BRULEUR #2 " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 5 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 50.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6785 | FT004C317() | HPM | FULL | "DEBIT AIR BRULEUR #3 " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 6 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 50.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6825 | FT004D317() | HPM | FULL | "DEBIT AIR BRULEUR #4 " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 7 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 50.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6865 | FT005317() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #7" | "m3/h " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 8 |  | HLAI | 1_5_V | SQRROOT | DIRECT | 11070.00 | 0.000000 | D0 | 13284.00 | -2214.00 | CLAMP | 0.000000 |  | 0.000000
6889 | PT030317() | HPM | FULL | "PRES.VAPEUR CHAUDIERE #7" | "Kpa " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 10 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1725.000 | 1035.000 | D1 | 1860.000 | 890.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1400.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6929 | AT080317() | HPM | COMPONNT | "CONTROLE O2 COMBUSTION " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 12 |  | HLAI | 1_5_V | LINEAR | DIRECT | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | -------- |  | 0.000000
6953 | AI082317() | HPM | FULL | "CO GAZ DE COMBUSTION " | "PPM " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 13 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D0 | 1200.000 | -200.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 500.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
6993 | AT008317() | HPM | FULL | "CONDUCTIVITE CHAUD. #7 " | "uMHOS " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 1 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 5000.000 | 0.000000 | D0 | 6000.000 | -1000.00 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7033 | TI800317() | HPM | FULL | "ENTREE AIR RECHAUFFEUR " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 10 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 62.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7073 | TI801317() | HPM | FULL | "SORTIE AIR RECHAUFFEUR " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 11 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 260.0000 | 0.000000 | D1 | 312.0000 | -52.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 200.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7113 | TI802317() | HPM | FULL | "ENTREE GAZ RECHAUFEUR " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 12 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 426.0000 | 0.000000 | D1 | 511.0000 | -85.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 316.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | DISABLE
7153 | TI803317() | HPM | FULL | "SORTIE GAZ RECHAUFEUR " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 13 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 200.0000 | 0.000000 | D1 | 240.0000 | -40.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 180.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | DISABLE
7193 | TT804317() | HPM | FULL | "TEMPERATURE MAZOUT CH#7 " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 9 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 300.0000 | 0.000000 | D1 | 360.0000 | -60.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 121.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7233 | TT805317() | HPM | FULL | "TEMP. AIR CHEMINEE CH7" | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 15 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 200.0000 | 0.000000 | D1 | 240.0000 | -40.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 120.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7273 | DI084317() | HPM | FULL | "DENSITE MAZOUT CH#7 " | "g/cc " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 16 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1.250000 | 0.750000 | D2 | 1.350000 | 0.750000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7435 | TI804317() | HPM | FULL | "TEMPERATURE MAZOUT CH#7 " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 14 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 300.0000 | 0.000000 | D1 | 360.0000 | -60.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 121.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7503 | PI058317() | HPM | FULL | "PRES. GAZ BRULEURS CH7" | "Kpa " | " " | "C7 " | " " | C7 | 01 | 7 | 6 | 8 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 420.0000 | 0.000000 | D1 | 504.0000 | -84.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 186.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 206.0000 | -------- | -------- | -------- | LOW | ENABLE | NOACTION | CUTOUT | 240.0000 | NOACTION | CUTOUT
7548 | AT008319() | HPM | FULL | "CONDUCTIVITE CHAUD. #9 " | "uMHOS " | " " | " " | " " | C9 | 01 | 7 | 1 | 6 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 5000.000 | 0.000000 | D0 | 6000.000 | -1000.00 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7606 | AT080319() | HPM | FULL | "CONTROLE O2 COMBUSTION " | "% " | " " | "C9 " | " " | C9 | 01 | 7 | 5 | 11 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 20.00000 | 0.000000 | D1 | 24.00000 | -4.00000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 5.250000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 9.500000 | 1.000000 | -------- | -------- | LOW | ENABLE | HIGH | CUTOUT | -------- |  |  | HIGH | CUTOUT | --------
7652 | AI082319() | HPM | FULL | "CO GAZ DE COMBUSTION " | "PPM " | " " | "C9 " | " " | C9 | 01 | 7 | 5 | 12 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 5000.000 | 0.000000 | D0 | 6000.000 | -5000.00 | CLAMP | -------- | ONLYAUTO | 0.000000 | 500.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 1200.000 | -------- | -------- | -------- | LOW | ENABLE | HIGH | CUTOUT | --------
7695 | LT001319() | HPM | FULL | "NIVEAU CHAUDIERE #9" | "mmH2O " | " " | "C9 " | " " | C9 | 01 | 7 | 1 | 1 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | -400.000 | D1 | 480.0000 | -480.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 45.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 200.0000 | -200.000 | -------- | -------- | LOW | ENABLE | EMERGNCY | CUTOUT | -------- |  |  | EMERGNCY | CUTOUT | --------
7790 | TI805318() | HPM | FULL | "TEMP. AIR CHEMINEE CH8" | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 7 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 500.0000 | 0.000000 | D1 | 600.0000 | -200.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 182.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7830 | TT822318() | HPM | FULL | "ENTREE EAU RECHAUFFEUR " | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 9 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 260.0000 | 0.000000 | D0 | 310.0000 | -50.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 105.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7888 | LT001318() | HPM | FULL | "NIVEAU CHAUDIERE #8" | "mmH2O " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 8 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 400.0000 | -400.000 | D1 | 480.0000 | -480.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7928 | FT002318() | HPM | FULL | "DEBIT EAU CHAUDIERE #8" | "Kg/h " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 9 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 117000.0 | 0.000000 | D0 | 140000.0 | -23400.0 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
7968 | FT004318() | HPM | FULL | "DEBIT AIR BRULEUR CH8 " | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 11 | -- | HLAI | 1_5_V | SQRROOT | DIRECT | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8008 | FT005318() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #8" | "m3/h " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 12 |  | HLAI | 1_5_V | LINEAR | DIRECT | 9000.000 | 0.000000 | D0 | 10800.00 | -1800.00 | CLAMP | 0.000000 |  | 0.000000
8032 | PT030318() | HPM | FULL | "PRES.VAPEUR CHAUDIERE #8" | "kPa " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 14 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1725.000 | 0.000000 | D0 | 2070.000 | -345.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 1400.000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8072 | PDT031318() | HPM | FULL | "PRES.DIF.VAP ATOMISANTE " | "kPa " | " " | "C8 " | " " | C8 | 01 | 7 | 1 | 15 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 500.0000 | 0.000000 | D1 | 600.0000 | -100.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 0.000000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8112 | AT008318() | HPM | FULL | "CONDUCTIVITE CHAUD. #8 " | "uMHOS " | " " | "C8 " | " " | C8 | 01 | 7 | 4 | 5 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 5000.000 | 0.000000 | D0 | 6000.000 | -1000.00 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8152 | AT080318() | HPM | COMPONNT | "CONTROLE O2 COMBUSTION " | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 4 | 12 |  | HLAI | 1_5_V | LINEAR | DIRECT | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | -------- |  | 0.000000
8176 | TI807318() | HPM | FULL | "TEMP. TUBES CHAUDIERE #8" | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 8 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1094.000 | 0.000000 | D0 | 1300.000 | -200.000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 255.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8216 | TI823318() | HPM | FULL | "SORTIE EAU RECHAUFFEUR " | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 10 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 260.0000 | 0.000000 | D0 | 310.0000 | -50.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 166.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8364 | II_URGO_319() | HPM | FULL | "COURANT GENERATRICE " | "AMPAIRS " | "GEN.URGO" | " " | " " | C9 | 01 | 7 | 7 | 16 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 1000.000 | 0.000000 | D0 | 1200.000 | -200.000 | CLAMP | -------- | ONLYAUTO | 0.000000 | 500.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | EMERGNCY | ENABLE
8450 | TI824318() | HPM | FULL | "ENTREE #1 ECONOMISEUR " | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 14 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 300.0000 | 0.000000 | D0 | 310.0000 | -50.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 167.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8490 | TI825318() | HPM | FULL | "ENTREE #2 ECONOMISEUR " | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 15 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 300.0000 | 0.000000 | D0 | 310.0000 | -50.0000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 172.0000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
8530 | FT005319() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #9" | "m3/h " | " " | "C9 " | " " | C9 | 01 | 7 | 1 | 4 |  | HLAI | 1_5_V | SQRROOT | DIRECT | 4672.280 | 0.000000 | D0 | 5608.000 | -934.000 | CLAMP | 0.000000 |  | 0.000000
8554 | TI008330() | HPM | FULL | "TEMP. SOUS- STATION310-4" | "DEG C " | " " | "C7 " | " " | C7 | 01 | 7 | 7 | 1 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 50.00000 | 0.000000 | D1 | 60.00000 | -5.00000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | 25.00000 | 25 | -- | NONE | NONE | 0 | 0 | ONE | 35.00000 | 5.000000 | -------- | -------- | LOW | ENABLE | HIGH | CUTOUT | -------- |  |  | NOACTION | CUTOUT | --------
8600 | PT013317() | HPM | COMPONNT | "PRES.AIR FORCE CH#7 " | "PO H20 " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 14 |  | HLAI | 1_5_V | LINEAR | DIRECT | 25.00000 | 0.000000 | D1 | 35.00000 | -2.50000 | NOCLAMP | -------- |  | 0.000000
8624 | PT014317() | HPM | COMPONNT | "PRE.AIR ENT.ECHAN. CH#7 " | "PO H20 " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 15 |  | HLAI | 1_5_V | LINEAR | DIRECT | 25.00000 | 0.000000 | D1 | 35.00000 | -2.50000 | NOCLAMP | -------- |  | 0.000000
8648 | PI041317() | HPM | FULL | "PRES.AIR VERSBRULEURS C7" | "PO H20 " | " " | "C7 " | " " | C7 | 01 | 7 | 2 | 16 | -- | HLAI | 1_5_V | LINEAR | DIRECT | 20.00000 | 0.000000 | D1 | 21.50000 | -1.50000 | NOCLAMP | -------- | ONLYAUTO | 0.000000 | -------- | 25 | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE

## HPM7 ANOUTNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PNTMODTY | OPTDIR | OPCHAR | $OPTOL | OUTIND | $OLDEVDS
7313 | LV001317() | HPM | COMPONNT | "NIVEAU CHAUDIERE #7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | 1 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7331 | FV005317() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | 4 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7349 | FV006317() | HPM | COMPONNT | "DEBIT MAZOUT CHAUD. #7 " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | 5 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7367 | PV030317() | HPM | COMPONNT | "PRES.VAPEUR CHAUDIERE #7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | 6 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
7385 | AV008317() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #7 " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 20 | 7 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7403 | TV805317() | HPM | COMPONNT | "TEMP. AIR CHEMINEE CH7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 20 | 9 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7588 | AV008319() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #9 " | "% " | " " | " " | " " | C9 | 01 | 7 | 12 | 5 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7741 | PO310319() | HPM | COMPONNT | "PO MAITRE CHAUDIERE #9" | "% " | " " | "C9 " | " " | C9 | 01 | 7 | 12 | 16 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
7870 | TV822318() | HPM | COMPONNT | "TEMP. AIR CHEMINEE CH8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 20 | 6 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8256 | LV001318() | HPM | COMPONNT | "NIVEAU CHAUDIERE #8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 12 | 7 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8274 | FZ004318() | HPM | COMPONNT | "DEBIT AIR CHAUDIERE #8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 12 | 8 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8292 | FV005318() | HPM | COMPONNT | "DEBIT GAZ CHAUDIERE #8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 12 | 9 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8310 | FV006318() | HPM | COMPONNT | "DEBIT MAZOUT CHAUD. #8 " | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 12 | 10 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8328 | PV030318() | HPM | COMPONNT | "PRES.VAPEUR CHAUDIERE #8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 12 | 11 | AO_16 | REVERSE | OFF | 0.000000 | DIRECT | ENABLE
8346 | PDV031318() | HPM | COMPONNT | "PRES.DIF.VAP ATOMISANTE " | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 12 | 12 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8404 | AV008318() | HPM | COMPONNT | "CONDUCTIVITE CHAUD. #8 " | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 20 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8688 | PDZ013317() | HPM | COMPONNT | "VOLET PRESSIDIFF AIR FOR" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | 2 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE
8706 | FZ004317() | HPM | COMPONNT | "VOLETS DEBITAIR COMB CH7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | 3 | AO_16 | DIRECT | OFF | 0.000000 | DIRECT | ENABLE

## HPM7 ARRAY
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | EXTDATA | IOPNUM | FTANUM | DEVADDR | SCANPRI | AUXDATA1 | AB_DATA1 | AUXDATA2 | AB_DATA2 | AUXDATA3 | AB_DATA3 | AUXDATA4 | AB_DATA4 | FLSTIX | NFLAG | NNSTIX | NNUMERIC | STRSTIX | STRLEN | NSTRING | TIMESTIX | NTIME | SPLOCK | FLDESC | NNDESC | STRDESC | TIMEDESC | $ADD | STR32(001) | STR32(002) | STR32(003) | STR32(004) | STR32(005) | STR32(006) | STR32(007) | STR32(008) | STR32(009) | STR32(010) | STR32(011) | STR32(012) | STR32(013) | STR32(014) | STR32(015) | STR32(016) | STR32(017) | STR32(018) | STR32(019) | STR32(020) | STR32(021) | STR32(022) | STR32(023) | STR32(024) | STR32(025) | STR32(026) | STR32(027) | STR32(028) | STR32(029) | STR32(030) | STR32(031) | STR32(032) | STR32(033) | STR32(034) | STR32(035) | STR32(036) | STR32(037) | STR32(038) | STR32(039) | STR32(040) | STR32(041) | STR32(042) | STR32(043) | STR32(044) | STR32(045) | STR32(046) | STR32(047) | STR32(048) | STR32(049) | STR32(050) | STR32(051) | STR32(052) | STR32(053) | STR32(054) | STR32(055) | STR32(056) | STR32(057) | STR32(058) | STR32(059) | STR32(060) | STR32(061) | STR32(062) | STR32(063) | STR32(064) | STR32(065) | STR32(066) | STR32(067) | STR32(068) | STR32(069) | STR32(070) | STR32(071) | STR32(072) | STR32(073) | STR32(074) | STR32(075) | STR32(076) | STR32(077) | STR32(078) | STR32(079) | STR32(080) | STR32(081) | STR32(082) | STR32(083) | STR32(084) | STR32(085) | STR32(086) | STR32(087) | STR32(088) | STR32(089) | STR32(090) | STR32(091) | STR32(092) | STR32(093) | STR32(094) | STR32(095) | STR32(096) | STR32(097) | STR32(098) | STR32(099) | STR32(100) | STR32(101) | STR32(102) | STR32(103) | STR32(104) | STR32(105) | STR32(106) | STR32(107) | STR32(108) | STR32(109) | STR32(110) | STR32(111) | STR32(112) | STR32(113) | STR32(114) | STR32(115) | STR32(116) | STR32(117) | STR32(118) | STR32(119) | STR32(120) | STR32(121) | STR32(122) | STR32(123) | STR32(124) | STR32(125) | STR32(126) | STR32(127) | STR32(128) | STR32(129)
2 | FL_1_ACH8() | HPM | FULL | "COMM. 128 FLAG ACH8 " | "MODBUS " | " " | " " | C8 | 01 | 7 | 0 | 1 | -- | "----------------" | IO_FL | 14 | 1 | 102.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 5745 | 128 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ACH8 MODBUS 128 BIT A PARTIR DE 360-01 A 367-16 " | " " | " " | " " | ON
127 | FIFO_STR_C8() | HPM | FULL | "ARRAY ASCII POUR FIFO C8" | "FIFO_STR" | " " | " " | C8 | 01 | 7 | 0 | 21 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 641.0 | 32 | 160 | 0.00 | 0 | ENGINEER | " " | " " | "ARRAY ASCII STRING(32) POUR FIFO C8 " | " " | ON | "ERREUR DU CPU SYMAX " | "PSL052318 GAZ " | "PSL060318 MAZOUT " | "PSH058318 GAZ " | "SELECTEUR GAZ " | "DETECT. FLAMME GAZ C8 " | "PSH042318 FOYER " | "FSL004318 AIR COMBUSTION " | "ZS066318 BEC FERME " | "LSLL011318 COLLONNE D'EAU " | "PSH031318 BALLON " | "SEQUENCE PURGE " | "PSL499318 AIR INSTRUMENTS " | "TSL804318 MAZOUT " | "PSL031318 VAPEUR ATOMISANTE " | "SLECTEUR MAZOUT " | "8X1 VENTILATEUR AIR FORCE " | "DISJONCTEUR LI 35B/D1 " | "DISJONCTEUR L2 CB-1 " | "HS002318 ARRET URGENCE " | "HS010318 BOUTON ARRET BRULEUR " | "DETECT.FLAMME MAZOUT C8 " | "0023 FUTUR " | "0024 FUTUR "
1219 | FL_1_ACH7() | HPM | FULL | "COMM. 240 FLAG ACH7 " | "MODBUS " | " " | " " | C7 | 01 | 7 | 0 | 3 | -- | "----------------" | IO_FL | 14 | 2 | 8.000 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.20 | -------- | 1745 | 240 | 0.000 | 0 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ACH7 MODBUS 240 BIT A PARTIR DE 1745 A 1984 " | " " | " " | " " | ON
1348 | NN_1_ACH7() | HPM | FULL | "COMM. 16 REGISTRE ACH7 " | "MODBUS " | " " | " " | C7 | 01 | 7 | 0 | 4 | -- | "----------------" | IO_NN | 14 | 2 | 8.000 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.20 | -------- | 0.000 | 0 | 43000 | 16 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | "COMM.PLC ACH7 MODBUS 16 REGISTRE DE 43000 A 43015 " | " " | " " | " " | ON
3186 | FIFO_STR_C7() | HPM | FULL | "ARRAY ASCII POUR FIFO C7" | "FIFO_STR" | " " | " " | C7 | 01 | 7 | 0 | 20 | -- | "----------------" | NONE | [12 empty] | 0.000 | 0 | 0.000 | 0 | 1.000 | 32 | 160 | 0.00 | 0 | ENGINEER | " " | " " | "ARRAY ASCII STRING(32) POUR FIFO C7 " | " " | ON | "3489 YT091A317 REGIME AUTO #1 " | "3490 YT091B317 REGIME AUTO #2 " | "3491 F3-B8 VENT. AIR FORCE " | "3492 SECT.3-B8 VENT.AIR FORCE " | "3493 HS009317 BOUTON ARRET 3-B8 " | "3494 BOUTON ARRET 3-B8 PRET MOT." | "3495 ZS053B317 V.PRINC.GAZ FERME" | "3496 ZS054A317 V.EVENT OUVERTE " | "3497 ZS055B317 V.PRINC.GAZ FERME" | "3498 ZS063B317 V.PRINC.MZ. FERME" | "3499 ZS062A317 V RECIR.MZ.OUVERT" | "3500 LSLL011317 T.BAS.NIV.BALLON" | "3501 PSH032317 HAUTE PRES.BALLON" | "3502 PSH042317 H.PRESSION FOYER " | "3503 PSL041317 B.PRES.AIR FORCE " | "3504 YT091C317 REGIME AUTO #3 " | "3505 YT091D317 REGIME AUTO #4 " | "3506 HS011317 SEL.AUTO-MAN BRUL." | "3507 FUTUR " | "3508 FUTUR " | "3509 FUTUR " | "3510 FUTUR " | "3511 FUTUR " | "3512 FUTUR " | "3513 FUTUR " | "3514 FUTUR " | "3515 FUTUR " | "3516 FUTUR " | "3517 FUTUR " | "3518 FUTUR " | "3519 FUTUR " | "3520 FUTUR " | "3521 FUTUR " | "3522 FUTUR " | "3523 FUTUR " | "3524 HS013317 BOUTON ARRET BR#1 " | "3525 ARRET BRULEUR#1 VIA DCS " | "3526 BS090A317 PERTE DE FLAMME " | "3527 ZS404A317 REGIS.BR#1 FERME " | "3528 ZS056E317 V.GAZ BR#1 FERME " | "3529 ZS057A317 V.MAN.GAZ B1.FERM" | "3530 ZS064E317 V.MAZ BR#1 FERME " | "3531 ZS065A317 V.ATOMIS.BR#1 " | "3532 FUTUR " | "3533 FUTUR " | "3534 FUTUR " | "3535 FUTUR " | "3536 FUTUR " | "3537 FUTUR " | "3538 FUTUR " | "3539 FUTUR " | "3540 FUTUR " | "3541 FUTUR " | "3542 FUTUR " | "3543 FUTUR " | "3544 FUTUR " | "3545 FUTUR " | "3546 FUTUR " | "3547 FUTUR " | "3548 FUTUR " | "3549 FUTUR " | "3550 FUTUR " | "3551 FUTUR " | "3552 HS016317 BOUTON ARRET BR#2 " | "3553 ARRET BRULEUR#2 VIA DCS " | "3554 BS090B317 PERTE DE FLAMME " | "3555 ZS404B317 REGIS.BR#2 FERME " | "3556 ZS056F317 V.GAZ BR#2 FERME " | "3557 ZS057B317 V.MAN.GAZ FERME " | "3558 ZS064F317 V.MAZ.BR#2 FERME " | "3559 ZS065B317 V.ATOMIS.BR#2 " | "3560 FUTUR " | "3561 FUTUR " | "3562 FUTUR " | "3563 FUTUR " | "3564 FUTUR " | "3565 FUTUR " | "3566 FUTUR " | "3567 FUTUR " | "3568 FUTUR " | "3569 FUTUR " | "3570 FUTUR " | "3571 FUTUR " | "3572 FUTUR " | "3573 FUTUR " | "3574 FUTUR " | "3575 FUTUR " | "3576 FUTUR " | "3577 FUTUR " | "3578 FUTUR " | "3579 FUTUR " | "3580 HS019317 BOUTON ARRET BR#3 " | "3581 ARRET BRULEUR #3 VIA DCS " | "3582 BS090C317 PERTE DE FLAMME " | "3583 ZS404C317 REGIS.BR#3 FERME " | "3584 ZS056G317 V.GAZ BR#3 FERME " | "3585 ZS057C317 V.GAZ.MAN.FERME " | "3586 ZS064G317 V.MAZ.BR#3 FERME " | "3587 ZS065C317 V.ATOMIS.BR#3 " | "3588 FUTUR " | "3589 FUTUR " | "3590 FUTUR " | "3591 FUTUR " | "3592 FUTUR " | "3593 FUTUR " | "3594 FUTUR " | "3595 FUTUR " | "3596 FUTUR " | "3597 FUTUR " | "3598 FUTUR " | "3599 FUTUR " | "3600 FUTUR " | "3601 FUTUR " | "3602 FUTUR " | "3603 FUTUR " | "3604 FUTUR " | "3605 FUTUR " | "3606 FUTUR " | "3607 FUTUR " | "3608 HS022317 BOUTON ARRET BR#4 " | "3609 ARRET BRULEUR #4 VIA DCS " | "3610 BS090D317 PERTE DE FLAMME " | "3611 ZS404D317 REGIS BR#4 FERME " | "3612 ZS056H317 V.GAZ.BR#4 FERME " | "3613 ZS057D317 V.GAZ.MAN.FERME " | "3614 ZS064H317 V.MAZ.BR#4 FERME " | "3615 ZS065D317 V.ATOMIS.BR#4 " | "3616 FUTUR " | "3617 FUTUR "
5626 | NN_1_ACH8() | HPM | FULL | "COMM. 6 REGISTRES ACH8 " | "MODBUS " | " " | " " | C8 | 01 | 7 | 0 | 2 | -- | "----------------" | IO_NN | 14 | 1 | 102.0 | LOW | -------- | -------- | 5.000000 | -------- | 485.0000 | -------- | 19200.10 | -------- | 0.000 | 0 | 40700 | 6 | 0.000 | 8 | 0 | 0.00 | 0 | OPERATOR | " " | "COMM.PLC ACH8 MODBUS 6 REGISTRE A PARTIR DE 700 A 705 " | " " | " " | ON

## HPM7 DIINNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | PNTMODTY | DITYPE | STATETXT(1) | STATETXT(0) | BOXCLR(1) | BOXCLR(0) | INPTDIR | PVSRCOPT | $AUXUNIT | $REALARM | ALMOPT | PVNORMAL | $DLYOPT | DLYTIME | OFFNRMPR | $OFSELCT | ALENBST | EVTOPT
6151 | ALARME_CH9() | HPM | FULL | "ALARME CHAUDIERE #9" | " " | " " | "C9 " | " " | C9 | 01 | 7 | 17 | 4 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | DIRECT | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
7421 | HS005_006317() | HPM | COMPONNT | "SELECTEUR GAZ / MAZOUT" | " " | " " | "C7 " | " " | C7 | 01 | 7 | 17 | 2 |  | DI | STATUS
7475 | YS006317() | HPM | COMPONNT | "TRANSFERT GAZ / MAZOUT" | " " | " " | "C7 " | " " | C7 | 01 | 7 | 17 | 3 |  | DI | STATUS
7489 | VC004317() | HPM | COMPONNT | "TRACKING PURGE BRULEURS " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 17 | 1 |  | DI | STATUS
7759 | 5_1A_1_364() | HPM | FULL | "POMPE ASSECHEMENT CLARIF" | " " | " " | "CE " | " " | CE | 01 | 7 | 17 | 32 | -- | DI | STATUS | "ALARME " | "NORMAL " | RED | GREEN | REVERSE | ONLYAUTO | -- | 0 | OFFNORML | NORMAL | PMOFFDLY | 5 | HIGH | CUTOUT | ENABLE | NONE
8422 | HS005_006318() | HPM | COMPONNT | "SELECTEUR GAZ / MAZOUT" | " " | " " | "C8 " | " " | C8 | 01 | 7 | 17 | 5 |  | DI | STATUS
8436 | VC004318() | HPM | COMPONNT | "TRACKING PURGE BRULEURS " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 17 | 6 |  | DI | STATUS

## HPM7 FLAGNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | STATETXT(1) | STATETXT(0) | PV | BOXCLR(1) | BOXCLR(0) | $AUXUNIT | $REALARM | OFFNRMPR | $OFSELCT | ALENBST | EIPPCODE
43 | LSHH011321() | HPM | FULL | "T.H.NIV.PUIT DEBORDEMENT" | " " | "PUIT DEB" | " " | " " | MZ | 01 | 7 | 5 | -- | "ALARME " | "NORMAL " | ALARME | RED | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
180 | BS090318() | HPM | FULL | "PERTE DE FLAMME GAZ C8 " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 43 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
203 | BS091318() | HPM | FULL | "PERTE DE FLAMME MZ C8 " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 44 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
1196 | PSH042317() | HPM | FULL | "HAUTE PRESSION FOYER " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 13 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2286 | FSL004317() | HPM | FULL | "BAS DEBIT AIR DE COMB." | " " | " " | "C7 " | " " | C7 | 01 | 7 | 7 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2309 | FSLL004317() | HPM | FULL | "T.BAS DEBIT AIR DE COMB." | " " | " " | "C7 " | " " | C7 | 01 | 7 | 8 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
2332 | LSH011317() | HPM | FULL | "HAUT NIV. BALLON " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 9 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2441 | LSL011317() | HPM | FULL | "BAS NIV. BALLON " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 10 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2464 | LSLL011317() | HPM | FULL | "TRES BAS NIV. BALLON " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 11 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2487 | PSH032317() | HPM | FULL | "HAUTE PRESSION BALLON " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 12 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2510 | PSH058317() | HPM | FULL | "HAUTE PRES. GAZ BRULEURS" | " " | " " | "C7 " | " " | C7 | 01 | 7 | 14 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2533 | PSH060317() | HPM | FULL | "H.PRES.MAZOUT BRULEURS " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 15 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2556 | PSH504317() | HPM | FULL | "HAUTE PRES. GAZ PILOT " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 16 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2579 | PSL031317() | HPM | FULL | "BASSE PRES. VAPEUR ATOM." | " " | " " | "C7 " | " " | C7 | 01 | 7 | 17 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2602 | PSL035317() | HPM | FULL | "B.PRES. VAPEUR SOUF.SUIE" | " " | " " | "C7 " | " " | C7 | 01 | 7 | 18 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2625 | PSL041317() | HPM | FULL | "BASSE.PRES. AIR FORCE " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 19 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2648 | PSL499317() | HPM | FULL | "B.PRES.AIR INSTRUMENT " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 20 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2671 | PSL052317() | HPM | FULL | "BASSE PRES.GAZ BRULEURS " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 21 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2739 | PSL060317() | HPM | FULL | "BAS.PRES.MAZOUT BRULEURS" | " " | " " | "C7 " | " " | C7 | 01 | 7 | 22 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2762 | PSL610317() | HPM | FULL | "B.PRES.LUB.RECHAUF.AIR " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 23 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
2785 | TSL804317() | HPM | FULL | "BASSE TEMP. MAZOUT " | " " | " " | "C7 " | " " | C7 | 01 | 7 | 24 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
3143 | YT001317() | HPM | FULL | "CONTOURNE PROTEC.COL.EAU" | " " | "PROTECT." | "C7 " | " " | C7 | 01 | 7 | 25 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
5281 | LSH011318() | HPM | FULL | "HAUT NIV. BALLON " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 26 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5304 | LSL011318() | HPM | FULL | "BAS NIV. BALLON " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 27 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5327 | LSLL011318() | HPM | FULL | "TRES BAS NIV. BALLON " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 28 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5350 | LSL010318() | HPM | FULL | "BAS NIV. HYDRASTEP " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 29 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5373 | LSLL010318() | HPM | FULL | "TRES BAS NIV. HYDRASTEP" | " " | " " | "C8 " | " " | C8 | 01 | 7 | 30 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5396 | PDSL031318() | HPM | FULL | "PRES.DIFF.VAP.ATOMISANTE" | " " | " " | "C8 " | " " | C8 | 01 | 7 | 31 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5419 | PSH032318() | HPM | FULL | "HAUTE PRESSION BALLON " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 32 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5442 | PSH042318() | HPM | FULL | "HAUTE PRESSION FOYER " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 33 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5465 | PSH058318() | HPM | FULL | "HAUTE PRES. GAZ BRULEURS" | " " | " " | "C8 " | " " | C8 | 01 | 7 | 34 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5488 | PSL031318() | HPM | FULL | "BASSE PRES. VAPEUR ATOM." | " " | " " | "C8 " | " " | C8 | 01 | 7 | 35 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5511 | PSL052318() | HPM | FULL | "BASSE PRES.GAZ BRULEURS " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 36 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5534 | PSL060318() | HPM | FULL | "BAS.PRES.MAZOUT BRULEURS" | " " | " " | "C8 " | " " | C8 | 01 | 7 | 37 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5557 | PSL499318() | HPM | FULL | "B.PRES.AIR INSTRUMENT " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 38 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5580 | TSL804318() | HPM | FULL | "BASSE TEMP. MAZOUT " | " " | " " | "C8 " | " " | C8 | 01 | 7 | 39 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | HIGH | CUTOUT | ENABLE | --
5603 | YT001318() | HPM | FULL | "CONTOURNE PROTEC.COL.EAU" | " " | "PROTECT." | "C8 " | " " | C8 | 01 | 7 | 40 | -- | "ALARME " | "NORMAL " | NORMAL | RED | GREEN | -- | 0 | EMERGNCY | CUTOUT | ENABLE | --
5667 | FSL004318() | HPM | FULL | "BAS DEBIT AIR DE COMB." | " " | " " | "C8 " | " " | C8 | 01 | 7 | 41 | -- | "ALARME " | "NORMAL " | ALARME | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --
5690 | FSH004318() | HPM | FULL | "HAUT DEBIT AIR DE COMB." | " " | " " | "C8 " | " " | C8 | 01 | 7 | 42 | -- | "ALARME " | "NORMAL " | NORMAL | YELLOW | GREEN | -- | 0 | LOW | CUTOUT | ENABLE | --

## HPM7 LOGICNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | USERID | LOGMIX | LISRC(1) | LISRC(2) | LISRC(3) | LISRC(4) | LISRC(5) | LISRC(6) | LISRC(7) | LISRC(8) | LISRC(9) | LISRC(10) | LISRC(11) | LISRC(12) | LIBADOPT | LOSRC(1) | LODSTN(1) | LOENBL(1) | LOSRC(2) | LODSTN(2) | LOENBL(2) | LOSRC(3) | LODSTN(3) | LOENBL(3) | LOSRC(4) | LODSTN(4) | LOENBL(4) | LOSRC(5) | LODSTN(5) | LOENBL(5) | LOSRC(6) | LODSTN(6) | LOENBL(6) | LOSRC(7) | LODSTN(7) | LOENBL(7) | LOSRC(8) | LODSTN(8) | LOENBL(8) | LOSRC(9) | LODSTN(9) | LOENBL(9) | LOSRC(10) | LODSTN(10) | LOENBL(10) | LOSRC(11) | LODSTN(11) | LOENBL(11) | LOSRC(12) | LODSTN(12) | LOENBL(12) | NODESC | $AUXUNIT | $REALARM | ALENBST | C1PR | C1DESC | C1SRC | C2PR | C2DESC | C2SRC | C3PR | C3DESC | C3SRC | C4PR | C4DESC | C4SRC | EIPPCODE | LOGALGID(1) | LOGALGID(2) | LOGALGID(3) | LOGALGID(4) | LOGALGID(5) | LOGALGID(6) | LOGALGID(7) | LOGALGID(8) | NN(001) | GENDESC(1) | PRMDESC(1) | GENDESC(2) | PRMDESC(2) | S1(1) | S1(2) | GENDESC(3) | PRMDESC(3) | GENDESC(4) | PRMDESC(4) | S1(3) | S1(4) | GENDESC(5) | PRMDESC(5) | GENDESC(6) | PRMDESC(6) | GENDESC(7) | PRMDESC(7) | GENDESC(8) | PRMDESC(8) | S1(5) | S1(6) | S1(7) | S1(8) | S1REV(1) | S2(1) | S2REV(1) | S3(1) | S3REV(1) | S1REV(2) | S2(2) | S2REV(2) | S3(2) | S3REV(2) | FL(0007) | NN(002)
555 | ALARME7_1_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 7 | 1 | -- | "----------------" | 12_8_12 | --.-- | --.-- | --.-- | --.-- | FL_1_ACH8.FL(78) | --.-- | FL_1_ACH7.FL(60) | FL_1_ACH7.FL(61) | FL_1_ACH7.FL(85) | FL_1_ACH7.FL(86) | FL_1_ACH7.FL(87) | FL_1_ACH7.FL(88) | HOLD | L1 | --.-- | FL1 | L2 | --.-- | FL1 | L3 | --.-- | FL1 | L4 | --.-- | FL1 | L5 | LSHH011321.PVFL | FL2 | L6 | --.-- | FL1 | L7 | FSL004317.PVFL | FL2 | L8 | FSLL004317.PVFL | FL2 | L9 | LSH011317.PVFL | FL2 | L10 | LSL011317.PVFL | FL2 | L11 | LSLL011317.PVFL | FL2 | L12 | PSH032317.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
641 | PATCHOUT7_1() | HPM | COMPONNT | "TRANSFERT OUTPUT " | " " | " " | AX | 01 | 7 | 2 |  |  | 12_8_12 | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | [17 empty] | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
708 | TRACKINGS_7_2() | HPM | FULL | "TRACKINGS DU HPM_7 CH8 " | " " | " " | AX | 01 | 7 | 11 | -- | "----------------" | 12_8_12 | VC004318.PVFL | FFC004318.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L2 | FZ004318.OP | SO1 | NN1 | FZ004318.OP | SO2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 2 | -- | 0 | ENABLE | HIGH | " " | NONE | HIGH | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NULL | NULL | NULL | NULL | NULL | NULL | 100.0000 | "NORMAL " | SO1 | "TRACK " | SO2 | L1 | SO1
2808 | ALARME7_2_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 7 | 3 | -- | "----------------" | 12_8_12 | FL_1_ACH7.FL(89) | FL_1_ACH7.FL(90) | FL_1_ACH7.FL(91) | FL_1_ACH7.FL(92) | FL_1_ACH7.FL(93) | FL_1_ACH7.FL(94) | FL_1_ACH7.FL(95) | FL_1_ACH7.FL(96) | FL_1_ACH7.FL(97) | FL_1_ACH7.FL(98) | FL_1_ACH7.FL(99) | FL_1_ACH7.FL(100) | HOLD | L1 | PSH042317.PVFL | FL2 | L2 | PSH058317.PVFL | FL2 | L3 | PSH060317.PVFL | FL2 | L4 | PSH504317.PVFL | FL2 | L5 | PSL031317.PVFL | FL2 | L6 | PSL035317.PVFL | FL2 | L7 | PSL041317.PVFL | FL2 | L8 | PSL499317.PVFL | FL2 | L9 | PSL052317.PVFL | FL2 | L10 | PSL060317.PVFL | FL2 | L11 | PSL610317.PVFL | FL2 | L12 | TSL804317.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3057 | ALARME7_3_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 7 | 4 | -- | "----------------" | 12_8_12 | FL_1_ACH7.FL(172) | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | YT001317.PVFL | FL2 | L2 | --.-- | FL1 | L3 | --.-- | FL1 | L4 | --.-- | FL1 | L5 | --.-- | FL1 | L6 | --.-- | FL1 | L7 | --.-- | FL1 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
3344 | TRACKINGS_7_1() | HPM | FULL | "TRACKINGS DU HPM_7 CH7 " | " " | " " | AX | 01 | 7 | 5 | -- | "----------------" | 12_8_12 | VC004317.PVFL | FFC004317.OP | VC004317.PVFL | PDC013317.OP | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L2 | FZ004317.OP | SO1 | NN1 | FZ004317.OP | SO2 | L4 | PDZ013317.OP | SO3 | NN2 | PDZ013317.OP | SO4 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 4 | -- | 0 | ENABLE | HIGH | " " | NONE | HIGH | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NOT | NOT | NULL | NULL | NULL | NULL | 100.0000 NN(002)=100.0000 | "NORMAL " | SO1 | "TRACK " | SO2 | L1 | SO1 | "NORMAL " | SO3 | "TRACK " | SO4 | L3 | SO3
3443 | SELECT_GAZ_MZ_C7() | HPM | FULL | "SELECTEUR GAZ_MZ CH#7 " | " " | " " | C7 | 01 | 7 | 6 | -- | "----------------" | 12_8_12 | FY004B317.PVCALC | FY004C317.PVCALC | HS005_006317.PVFL | FT006317.PV | YS006317.PVFL | FY080A317.PVCALC | FY080B317.PVCALC | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | FY004D317.PV | SO1 | L2 | FY004D317.PV | SO2 | NN1 | FY006A317.PV | SO3 | L4 | FY006A317.PV | SO4 | L6 | FY080C317.PV | SO5 | L7 | FY080C317.PV | SO6 | NN1 | FY006F317.PV | SO7 | L4 | FY006F317.PV | SO8 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 8 | -- | 0 | ENABLE | HIGH | " " | NONE | HIGH | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NOT | NOT | NOT | NOT | NOT | NOT | 0.000000 | "GAZ " | SO1 | "MAZOUT " | SO2 | L3 | SO1 | "MAZOUT " | SO3 | "GAZ " | SO4 | L5 | SO3 | "MAZOUT " | SO5 | "GAZ " | SO6 | "MAZOUT " | SO7 | "GAZ " | SO8 | L3 | SO5 | L5 | SO7
3554 | SP_TRACK_C7() | HPM | FULL | "TRACKING DU SP HC310317 " | " " | " " | AX | 01 | 7 | 7 | -- | "----------------" | 12_8_12 | FY004G317.PVCALC | FFC004317.MANMODFL | FY005B317.PVCALC | FFC005317.MANMODFL | FY006C317.PVCALC | FFC006317.MANMODFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | FFC004317.SP | L2 | L3 | FFC005317.SP | L4 | L5 | FFC006317.SP | L6 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 2 | -- | 0 | ENABLE | HIGH | " " | NONE | HIGH | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL |  | "NORMAL " | SO1 | "TRACK " | SO2
4481 | SELECT_GAZ_MZ_C8() | HPM | FULL | "SELECTEUR GAZ_MZ CH#8 " | " " | " " | C8 | 01 | 7 | 8 | -- | "----------------" | 12_8_12 | FY004A318.PVCALC | FY004B318.PVCALC | HS005_006318.PVFL | FT006318.PV | FY080A318.PVCALC | FY080B318.PVCALC | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | L1 | FY004C318.PV | SO1 | L2 | FY004C318.PV | SO2 | NN1 | FY006A318.PV | SO3 | L4 | FY006A318.PV | SO4 | L5 | FY080C318.PV | SO5 | L6 | FY080C318.PV | SO6 | NN1 | FY006F318.PV | SO7 | L4 | FY006F318.PV | SO8 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | 8 | -- | 0 | ENABLE | HIGH | " " | NONE | HIGH | " " | NONE | NOACTION | " " | NONE | NOACTION | " " | NONE | -- | NOT | NOT | NOT | NOT | NOT | NOT | NOT | NOT | 0.000000 | "GAZ " | SO1 | "MAZOUT " | SO2 | L3 | SO1 | "MAZOUT " | SO3 | "GAZ " | SO4 | L3 | SO3 | "MAZOUT " | SO5 | "GAZ " | SO6 | "MAZOUT " | SO7 | "GAZ " | SO8 | L3 | SO5 | L3 | SO7
5713 | ALARME7_4_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 7 | 9 | -- | "----------------" | 12_8_12 | FL_1_ACH8.FL(74) | FL_1_ACH8.FL(75) | FL_1_ACH8.FL(77) | FL_1_ACH8.FL(79) | FL_1_ACH8.FL(80) | FL_1_ACH8.FL(81) | FL_1_ACH8.FL(82) | FL_1_ACH8.FL(83) | FL_1_ACH8.FL(85) | FL_1_ACH8.FL(86) | FL_1_ACH8.FL(87) | FL_1_ACH8.FL(88) | HOLD | L1 | FSH004318.PVFL | FL2 | L2 | FSL004318.PVFL | FL2 | L3 | LSH011318.PVFL | FL2 | L4 | LSL010318.PVFL | FL2 | L5 | LSL011318.PVFL | FL2 | L6 | LSLL010318.PVFL | FL2 | L7 | LSLL011318.PVFL | FL2 | L8 | PDSL031318.PVFL | FL2 | L9 | PSH032318.PVFL | FL2 | L10 | PSH042318.PVFL | FL2 | L11 | PSH058318.PVFL | FL2 | L12 | PSL031318.PVFL | FL2 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | NULL | NULL | NULL | NULL | NULL | NULL | NULL | NULL
5799 | ALARME7_5_PLC() | HPM | FULL | "ALARMES VENANT DES PLC " | " " | " " | AX | 01 | 7 | 10 | -- | "----------------" | 12_8_12 | FL_1_ACH8.FL(89) | FL_1_ACH8.FL(90) | FL_1_ACH8.FL(91) | FL_1_ACH8.FL(92) | FL_1_ACH8.FL(93) | FL_1_ACH8.FL(111) | FL_1_ACH8.FL(112) | FL_1_ACH8.FL(52) | FL_1_ACH8.FL(53) | --.-- | --.-- | --.-- | HOLD | L1 | PSL052318.PVFL | FL2 | L2 | PSL060318.PVFL | FL2 | L3 | PSL499318.PVFL | FL2 | L4 | TSL804318.PVFL | FL2 | L5 | YT001318.PVFL | FL2 | SO1 | BS090318.PVFL | FL2 | SO2 | BS091318.PVFL | FL2 | L8 | --.-- | FL1 | L9 | --.-- | FL1 | L10 | --.-- | FL1 | L11 | --.-- | FL1 | L12 | --.-- | FL1 | 0 | -- | 0 | ENABLE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | LOW | " " | NONE | -- | AND | AND | NULL | NULL | NULL | NULL | NULL | NULL | [5 empty] | L6 | L7 | [18 empty] | ON | L8 | OFF | FL2 | OFF | ON | L9 | OFF | FL2 | OFF
5936 | PROTECTION_C7_1() | HPM | COMPONNT | "PROTECTION CHAUDIERE #7 " | "C7 " | " " | C7 | 01 | 7 | 12 |  |  | 12_8_12 | FFC006317.BADCTLFL | FFC005317.BADCTLFL | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | --.-- | HOLD | SO1 | HC310317.SHUTDOWN | FL2 | SO2 | AC080317.SHUTDOWN | FL2 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | FL1 | --.-- | FL1 | [17 empty] | OR | OR | NULL | NULL | NULL | NULL | NULL | NULL | 0.000000 |  |  |  |  | L1 | L1 | [18 empty] | OFF | L2 | OFF | FL1 | OFF | OFF | L2 | OFF | FL1 | OFF | ON | 100.0000

## HPM7 NUMERNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PV | PVFORMAT
409 | FY080C318() | HPM | COMPONNT | "TRANSFERT GAZ_MZ_SP SO2 " | " " | " " | " " | " " | C8 | 01 | 7 | 14 | 10.00000 | D1
422 | FY080C317() | HPM | COMPONNT | "TRANSFERT GAZ_MZ_SP SO2 " | " " | " " | " " | " " | C7 | 01 | 7 | 10 | 4.275730 | D1
908 | HIER_FQ003317() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C7 " | " " | C7 | 01 | 7 | 1 | 1043040 | D1
921 | HIER_FQ003318() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C8 " | " " | C8 | 01 | 7 | 2 | 0.000000 | D1
934 | HIER_FQ003319() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C9 " | " " | C9 | 01 | 7 | 3 | 0.000000 | D1
1031 | HIER_FQ050317() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 7 | 15 | 0.000000 | D1
1044 | HIER_FQ050318() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 7 | 16 | 0.000000 | D1
1057 | HIER_FQ050319() | HPM | COMPONNT | "INTEGRATION D'HIER " | "m3 " | " " | "GN " | " " | GN | 01 | 7 | 17 | 0.000000 | D1
1157 | HIER_FQ006317() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C7 " | " " | C7 | 01 | 7 | 4 | 0.000000 | D1
1170 | HIER_FQ006318() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C8 " | " " | C8 | 01 | 7 | 5 | 0.000000 | D1
1183 | HIER_FQ006319() | HPM | COMPONNT | "INTEGRATION D'HIER " | "KG " | " " | "C9 " | " " | C9 | 01 | 7 | 6 | 0.000000 | D1
1669 | FY004D317() | HPM | COMPONNT | "DEBIT AIR/GAZ_MAZOUT CH7" | "% " | " " | " " | " " | C7 | 01 | 7 | 7 | 27.69410 | D1
1935 | FY006A317() | HPM | COMPONNT | "ZERO FLOW MAZOUT CH7 " | " " | " " | " " | " " | C7 | 01 | 7 | 8 | 0.000000 | D1
3672 | FY006F317() | HPM | COMPONNT | "ZERO FLOW_FQ_MZ_CH7 " | " " | " " | " " | " " | C7 | 01 | 7 | 9 | 0.000000 | D1
4177 | FY004C318() | HPM | COMPONNT | "DEBIT AIR/GAZ_MAZOUT CH8" | "% " | " " | " " | " " | C7 | 01 | 7 | 11 | -19.4300 | D1
4468 | FY006A318() | HPM | COMPONNT | "ZERO FLOW MAZOUT CH8 " | " " | " " | " " | " " | C8 | 01 | 7 | 12 | 0.000000 | D1
5001 | FY006F318() | HPM | COMPONNT | "ZERO FLOW_FQ_MZ_CH8 " | " " | " " | " " | " " | C8 | 01 | 7 | 13 | 0.000000 | D1

## HPM7 PRMODNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | SLOTNUM | PRIMMOD | USERID | STRLEN | SEQSLTSZ | CNTLLOCK | SPLOCK | RSTROPT | ACP | CLBACK | SEQPR | TIME(001) | NN(001)
801 | INTEGRE7_1() | HPM | FULL | "TRANSFERT INTEGRE.MINUIT" | "INTEGRE " | " " | AX | 01 | 7 | 1 | -- | "----------------" | 8 | 50 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION | " 0-13:53:15"
3166 | FIFO_C7() | HPM | FULL | "FIFO CHAUDIERE 7 " | "FIFO " | " " | C7 | 01 | 7 | 3 | -- | "----------------" | 8 | 10 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION |  | 94.00000
5897 | FIFO_C8() | HPM | FULL | "FIFO CHAUDIERE 8 " | "FIFO " | " " | C8 | 01 | 7 | 4 | -- | "----------------" | 8 | 10 | ENGINEER | ENGINEER | OFF | -- | 0 | NOACTION |  | 21.00000
5917 | HPM7_PLC_1() | HPM | FULL | "TRANSFERT VERS LES PLC " | " " | " " | C7 | 01 | 7 | 2 | -- | "----------------" | 8 | 20 | OPERATOR | OPERATOR | OFF | -- | 0 | NOACTION

## HPM7 REGCLNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | CTLALGID | PVEUHI | PVEULO | PVFORMAT | PVSRCOPT | OVERVAL | BADCTLOP | RCASOPT | NMODE | NMODATTR | MODEPERM | $MODESEL(1) | $MODESEL(5) | $MODESEL(2) | $MODESEL(3) | $MODESEL(4) | $BADOCMD | EXTSWOPT | SPHILM | SPLOLM | $SPTOL | SP | SPOPT | RBOPT | PIDFORM | CTLEQN | PVTRACK | CTLACTN | GAINOPT | K | T1 | T2 | NOCINPTS | CISRC(1) | NOCOPTS | CODSTN(1) | OUTIND | OPHILM | OPLOLM | SAFEOP | OPMCHLM | OPROCLM | $OPTOL | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | BADOCOPT | OPALDB | OPHITP | OPLOTP | PVALDB | PVHITP | PVLOTP | PVROCPTP | PVROCNTP | BADPVPR | DEVHITP | DEVLOTP | ALENBST | PVSOURCE | FFOPT | KFF | CISRC(2) | PVHIPR | $HISELCT | PVLOPR | $LOSELCT | PVHHTP | PVHHPR | $HHSELCT | PVLLTP | PVSGCHTP | CVEUHI | CVEULO | B | RATE1 | XEUHI | XEULO | BADCTLPR | OPHIPR | DEVLOPR | $DLSELCT | RTHILM | RTLOLM | BSHILM | BSLOLM | RATIO | BIAS | OPLOPR
334 | TC805317() | HPM | FULL | "TEMP. AIR CHEMINEE C7 " | "degC " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 37 | -- | "----------------" | PID | 200.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 200.0000 | 0.000000 | 0.000000 | 125.0000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 2.500000 | 5.000000 | 0.000000 | 1 | TI803317.PV | 1 | TV805317.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | FIVE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
1260 | LC001317() | HPM | FULL | "NIVEAU CHAUDIERE #7" | "mmH2O " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 11 | -- | "----------------" | PIDFF | 400.0000 | -400.000 | D0 | ALL | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 400.0000 | -400.000 | 0.000000 | 20.00000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 3.200000 | 9.000000 | 0.000000 | 2 | LT001317.PV | 1 | FC002317.SP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 200.0000 | -160.000 | -------- | -------- | LOW | -------- | -------- | ENABLE | AUTO | ADD | 1.000000 | FY003317.PVCALC | HIGH | CUTOUT | HIGH | CUTOUT | 350.0000 | HIGH | CUTOUT | -------- | --------
1389 | FC002317() | HPM | FULL | "DEBIT EAU CHAUDIERE #7" | "kg/h " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 12 | -- | "----------------" | PID | 163300.0 | 0.000000 | D0 | ALL | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 163300.0 | 0.000000 | 0.000000 | 26282.40 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.600000 | 0.125000 | 0.000000 | 1 | FT002317.PV | 1 | LV001317.OP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE | AUTO
1727 | AC080317() | HPM | FULL | "CONTROLE O2 COMBUSTION " | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 35 | -- | "----------------" | PID | 10.00000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 10.00000 | 0.000000 | 0.000000 | 4.609630 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 1.000000 | 3.500000 | 0.000000 | 2 | AT080317.PV | 0 |  | DIRECT | 105.0000 | -5.00000 | 100.0000 | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 9.500000 | 1.000000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | FY080C317.PV | NOACTION | CUTOUT | NOACTION | CUTOUT | -------- |  |  | -------- |  | 100.0000 | 0.000000
1854 | HC310317() | HPM | FULL | "MAITRE CHAUDIERE #7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 36 | -- | "----------------" | AUTOMAN |  |  |  |  | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | ON |  | ON | ON | SHEDMAN | NONE | [7 empty] | EQA | [6 empty] | 1 | PC310310.OP | 0 |  | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- |  | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | [8 empty] | ENABLE | [15 empty] | 0.000000 | 2.000000 | 100.0000 | 0.000000 | LOW
2021 | FFC005317() | HPM | FULL | "DEBIT GAZ CHAUDIERE #7" | "MBTU/h " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 14 | -- | "----------------" | PID | 400.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 400.0000 | 0.000000 | 0.000000 | 92.12150 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.500000 | 0.250000 | 0.000000 | 2 | FY005_006A317.PV | 1 | FV005317.OP | DIRECT | 105.0000 | 10.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | 100.0000 | -------- | ONE | -------- | 31.30000 | -------- | -------- | LOW | -------- | 35.00000 | ENABLE |  |  |  | FY005B317.PVCALC |  |  | NOACTION | CUTOUT |  |  |  | -------- | [8 empty] | HIGH | EMERGNCY | CUTOUT
2160 | FFC006317() | HPM | FULL | "DEBIT MAZOUT CHAUDIERE#7" | "MBTU/h " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 15 | -- | "----------------" | PID | 400.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 400.0000 | 0.000000 | 0.000000 | 94.48830 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.200000 | 0.100000 | 0.000000 | 2 | FY005_006A317.PV | 1 | FV006317.OP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | 35.00000 | ENABLE |  |  |  | FY006C317.PVCALC | [17 empty] | EMERGNCY | CUTOUT
2355 | FFC004317() | HPM | FULL | "DEBIT AIR BRULEURS CH7" | "% " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 13 | -- | "----------------" | PID | 100.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | RSP | CAS | OPERATOR | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 100.0000 | 0.000000 | 0.000000 | 26.43300 | NONE | FIXRATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.210000 | 0.050000 | 0.000000 | 2 | FY004E317.PVCALC | 0 |  | DIRECT | 105.0000 | 16.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | 10.00000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | FY004G317.PVCALC |  |  | NOACTION | CUTOUT |  |  |  | -------- |  | 100.0000 | 0.000000 | [8 empty] | 100.0000 | 0.010000 | 50.00000 | -50.0000 | 1.000000 | 4.000000
2894 | AC008317() | HPM | FULL | "CONDUCTIVITE CHAUD. #7 " | "uMHOS " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 31 | -- | "----------------" | PID | 5000.000 | 0.000000 | D0 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 5000.000 | 0.000000 | 0.000000 | 3200.000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | DIRECT | LIN | 10.00000 | 10.00000 | 0.000000 | 1 | AT008317.PV | 1 | AV008317.OP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 4000.000 | 2900.000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  |  | LOW | CUTOUT | LOW | CUTOUT | -------- |  |  | --------
2975 | PC030317() | HPM | FULL | "PRES. VAPEUR CHAUDIERE#7" | "Kpa " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 32 | -- | "----------------" | PID | 1725.000 | 850.0000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 1725.000 | 850.0000 | 0.000000 | 1466.870 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 5.000000 | 4.000000 | 0.000000 | 1 | PT030317.PV | 1 | PV030317.OP | DIRECT | 105.0000 | 20.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | 20.00000 | ONE | 1700.000 | 850.0000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  |  | HIGH | CUTOUT | HIGH | CUTOUT | -------- |  |  | -------- | [17 empty] | HIGH
3685 | AC008319() | HPM | FULL | "CONDUCTIVITE CHAUD. #9 " | "uMHOS " | " " | " " | " " | C9 | 01 | 7 | 0 | 21 | -- | "----------------" | PID | 5000.000 | 0.000000 | D0 | ONLYAUTO | 25 | NO_SHED | NONE | NONE |  | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 5000.000 | 0.000000 | 0.000000 | 3400.000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | DIRECT | LIN | 5.000000 | 10.00000 | 0.000000 | 1 | AT008319.PV | 1 | AV008319.OP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 4500.000 | 3000.000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  |  | LOW | CUTOUT | LOW | CUTOUT | -------- |  |  | --------
3765 | HC310319() | HPM | FULL | "MAITRE CHAUDIERE #9" | "% " | " " | "C9 " | " " | C9 | 01 | 7 | 0 | 24 | -- | "----------------" | AUTOMAN |  |  |  |  | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | ON |  | ON | ON | SHEDMAN | NONE | [7 empty] | EQA | [6 empty] | 1 | PC310310.OP | 1 | PO310319.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- |  | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | [8 empty] | ENABLE | [15 empty] | 0.000000 | 0.000000 | 100.0000 | 0.000000 | LOW
3818 | TC822318() | HPM | FULL | "TEMP. EAU ALIM. CH#8 " | "degC " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 41 | -- | "----------------" | PID | 260.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 260.0000 | 0.000000 | 0.000000 | 65.00000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 2.500000 | 5.000000 | 0.000000 | 1 | TT822318.PV | 1 | TV822318.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | FIVE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE
3893 | LC001318() | HPM | FULL | "NIVEAU CHAUDIERE #8" | "mmH2O " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 6 | -- | "----------------" | PIDFF | 400.0000 | -400.000 | D0 | ALL | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 400.0000 | -400.000 | 0.000000 | -110.000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 3.000000 | 5.000000 | 0.000000 | 2 | LT001318.PV | 1 | FC002318.SP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 200.0000 | -185.000 | -------- | -------- | LOW | -------- | -------- | ENABLE | AUTO | ADD | 1.000000 | FY003318.PVCALC | HIGH | CUTOUT | HIGH | CUTOUT | 350.0000 | HIGH | CUTOUT | -------- | --------
3981 | FC002318() | HPM | FULL | "DEBIT EAU CHAUDIERE #8" | "kg/h " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 7 | -- | "----------------" | PID | 117000.0 | 0.000000 | D0 | ALL | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 117000.0 | 0.000000 | 0.000000 | 5397.090 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.600000 | 0.100000 | 0.000000 | 1 | FT002318.PV | 1 | LV001318.OP | DIRECT | 105.0000 | -6.90000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE | AUTO
4235 | AC080318() | HPM | FULL | "CONTROLE O2 COMBUSTION " | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 30 | -- | "----------------" | PID | 10.00000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 10.00000 | 0.000000 | 0.000000 | 10.00000 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.500000 | 1.000000 | 0.000000 | 2 | AT080318.PV | 0 |  | DIRECT | 100.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | 2.000000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | FY080C318.PV |  |  | NOACTION | CUTOUT |  |  |  | -------- |  | 100.0000 | 0.000000
4315 | HC310318() | HPM | FULL | "MAITRE CHAUDIERE #8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 39 | -- | "----------------" | AUTOMAN |  |  |  |  | 25 | NO_SHED | NONE | CAS | OPERATOR | PERMIT | ON | ON |  | ON | ON | SHEDMAN | NONE | [7 empty] | EQA | [6 empty] | 1 | PC310310.OP | 0 |  | DIRECT | 60.00000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- |  | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | [8 empty] | ENABLE | [15 empty] | 0.000000 | 2.000000 | 100.0000 | 0.000000 | LOW
4694 | FFC005318() | HPM | FULL | "DEBIT GAZ CHAUDIERE #8" | "MBTU/h " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 9 | -- | "----------------" | PID | 320.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 280.0000 | 0.000000 | 0.000000 | 0.000000 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.200000 | 0.100000 | 0.000000 | 2 | FY005_006A318.PVCALC | 1 | FV005318.OP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | FY005B318.PVCALC
4770 | FFC006318() | HPM | FULL | "DEBIT MAZOUT CHAUDIERE#8" | "MBTU/h " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 10 | -- | "----------------" | PID | 320.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | RSP | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 275.0000 | 0.000000 | 0.000000 | 0.000000 | NONE | NORATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.150000 | 0.100000 | 0.000000 | 2 | FY005_006A318.PVCALC | 1 | FV006318.OP | DIRECT | 105.0000 | -5.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | FY006C318.PVCALC
4918 | FFC004318() | HPM | FULL | "DEBIT AIR BRULEURS CH8" | "% " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 8 | -- | "----------------" | PID | 100.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | RSP | CAS | OPERATOR | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 100.0000 | 0.000000 | 0.000000 | 0.000000 | NONE | FIXRATBI | INTERACT | EQA | TRACK | REVERSE | LIN | 0.100000 | 0.100000 | 0.000000 | 2 | FY004D318.PVCALC | 0 |  | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | FY004F318.PVCALC | [9 empty] | 100.0000 | 0.000000 | [8 empty] | 100.0000 | 0.010000 | 50.00000 | -50.0000 | 1.000000 | 0.000000
5014 | AC008318() | HPM | FULL | "CONDUCTIVITE CHAUD. #8 " | "uMHOS " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 27 | -- | "----------------" | PID | 5000.000 | 0.000000 | D0 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 5000.000 | 0.000000 | 0.000000 | 3200.000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | DIRECT | LIN | 10.00000 | 40.00000 | 0.000000 | 1 | AT008318.PV | 1 | AV008318.OP | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | 4000.000 | 2900.000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  |  | LOW | CUTOUT | LOW | CUTOUT | -------- |  |  | --------
5095 | PC030318() | HPM | FULL | "PRES. VAPEUR CHAUDIERE#8" | "kPa " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 28 | -- | "----------------" | PID | 1725.000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 1725.000 | 0.000000 | 0.000000 | 1460.980 | NONE | NORATBI | INTERACT | EQA | TRACK | DIRECT | LIN | 5.000000 | 4.000000 | 0.000000 | 1 | PT030318.PV | 1 | PV030318.OP | DIRECT | 105.0000 | 20.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | 20.00000 | ONE | 1550.000 | 850.0000 | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  |  | HIGH | CUTOUT | HIGH | CUTOUT | -------- |  |  | -------- | [17 empty] | HIGH
5177 | PDC031318() | HPM | FULL | "PRES.DIF.VAP ATOMISANTE " | "kPa " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 29 | -- | "----------------" | PID | 500.0000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | CAS | NONE | PERMIT | ON | ON | ON | ON | ON | SHEDMAN | NONE | 500.0000 | 0.000000 | 0.000000 | 89.89880 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 0.500000 | 0.070000 | 0.000000 | 2 | PDT031318.PV | 1 | PDV031318.OP | DIRECT | 105.0000 | 10.00000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | ONE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE |  |  |  | PDY031318.PVCALC
6047 | PDC013317() | HPM | FULL | "PRESS DIFFERAIR FORCE " | "PO H2O " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 34 | -- | "----------------" | PID | 25.00000 | 0.000000 | D1 | ONLYAUTO | 25 | NO_SHED | NONE | AUTO | NONE | PERMIT | ON | OFF | ON | OFF | OFF | SHEDMAN | NONE | 7.000000 | 4.000000 | 0.000000 | 6.000000 | NONE | NORATBI | INTERACT | EQA | NOTRACK | REVERSE | LIN | 0.500000 | 0.200000 | 0.000000 | 1 | PDY013A317.PV | 0 |  | DIRECT | 105.0000 | 0.000000 | -------- | 0.000000 | -------- | 0.000000 | -- | NONE | NONE | 0 | 0 | OFF | 5.000000 | -------- | -------- | FIVE | -------- | -------- | -------- | -------- | LOW | -------- | -------- | ENABLE | [13 empty] | 100.0000 | 0.000000

## HPM7 REGPVNIM
Row | SYSTEM ENTITY | NODETYP | PNTFORM | PTDESC | EUDESC | KEYWORD | ASSOCDSP | $CDETAIL | UNIT | NTWKNUM | NODENUM | MODNUM | SLOTNUM | PRIMMOD | USERID | PVALGID | PVEUHI | PVEULO | PVFORMAT | PVEXEUHI | PVEXEULO | PVCLAMP | PVSRCOPT | TF | PVTV | OVERVAL | SEGTOT | IN0 | OUT0 | IN1 | OUT1 | IN2 | OUT2 | IN3 | OUT3 | IN4 | OUT4 | IN5 | OUT5 | IN6 | OUT6 | IN7 | OUT7 | IN8 | OUT8 | IN9 | OUT9 | IN10 | OUT10 | PISRC(1) | $AUXUNIT | $ALDLOPT | $DLBADAL | DLYTIME | $REALARM | PVALDB | PVHITP | PVLOTP | PVROCPTP | PVROCNTP | BADPVPR | ALENBST | PVEQN | ACCTYPE | TIMEBASE | C | RESETVAL | CUTOFFLM | AVTV | AVDEV1TP | N | C1 | C2 | C3 | C4 | CALCEXP | PISRC(2) | NMIN | FRCPERM | PISRC(3) | PISRC(4) | DEVHITP | IN11 | OUT11 | IN12 | OUT12 | D | PVLOPR | $LOSELCT | PVLLTP
66 | PDY031318() | HPM | FULL | "CARACTERISAT ATOMISATION" | "kPa " | " " | " " | " " | C8 | 01 | 7 | 0 | 26 | -- | "----------------" | GENLIN | 500.0000 | 0.000000 | D1 | 600.0000 | -100.000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 10 | 0.000000 | 90.00000 | 805.0000 | 100.0000 | 1584.000 | 130.0000 | 2000.000 | 130.0000 | 2889.000 | 150.0000 | 3588.000 | 150.0000 | 4222.000 | 150.0000 | 4935.000 | 150.0000 | 5613.000 | 140.0000 | 6011.000 | 140.0000 | 7130.000 | 140.0000 | FT006318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
226 | FY080A317() | HPM | FULL | "CARACTERISATION GAZ/O2 " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 16 | -- | "----------------" | GENLIN | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 6 | 0.000000 | 10.00000 | 1660.000 | 8.000000 | 2450.000 | 5.000000 | 3237.000 | 4.000000 | 4900.000 | 3.000000 | 5979.000 | 3.000000 | 8000.000 | 3.000000 | [8 empty] | FT005317.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
279 | FY080B317() | HPM | FULL | "CARACTERISATION MAZOU/O2" | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 18 | -- | "----------------" | GENLIN | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 7 | 1400.000 | 7.000000 | 2500.000 | 4.000000 | 3500.000 | 3.000000 | 4900.000 | 2.800000 | 5500.000 | 2.800000 | 6500.000 | 2.000000 | 7500.000 | 1.500000 | 10000.00 | 1.500000 | [6 empty] | FT006317.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
435 | FY080A318() | HPM | FULL | "CARACTERISATION GAZ/O2 " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 35 | -- | "----------------" | GENLIN | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 10 | 0.000000 | 10.00000 | 465.0000 | 10.00000 | 1466.000 | 6.500000 | 2114.000 | 5.400000 | 2838.000 | 4.500000 | 3495.000 | 4.100000 | 4072.000 | 3.400000 | 4980.000 | 3.300000 | 5560.000 | 3.200000 | 6242.000 | 3.200000 | 7055.000 | 3.000000 | FT005318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
496 | FY080B318() | HPM | FULL | "CARACTERISATION MAZOU/O2" | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 39 | -- | "----------------" | GENLIN | 10.00000 | 0.000000 | D1 | 12.00000 | -2.00000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 9 | 686.0000 | 8.000000 | 1321.000 | 6.500000 | 2023.000 | 5.500000 | 2590.000 | 5.000000 | 3173.000 | 4.500000 | 3747.000 | 3.500000 | 4219.000 | 3.400000 | 4536.000 | 3.400000 | 5478.000 | 3.400000 | 5800.000 | 3.300000 |  |  | FT006318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
821 | FQ003317() | HPM | COMPONNT | "DEBIT VAPEUR CHAUDIERE#7" | "KG " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 46 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT003317.PV | [12 empty] | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
850 | FQ003318() | HPM | COMPONNT | "DEBIT VAPEUR CHAUDIERE#8" | "KG " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 47 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT003318.PV | [12 empty] | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
879 | FQ003319() | HPM | COMPONNT | "DEBIT VAPEUR CHAUDIERE#9" | "KG " | " " | "C9 " | " " | C9 | 01 | 7 | 0 | 48 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT003319.PV | [12 empty] | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
947 | FQ050317() | HPM | COMPONNT | "DEBIT GAS CHAUDIERE #7" | "m3 " | " " | "GN " | " " | GN | 01 | 7 | 0 | 43 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT050317.PV | [12 empty] | EQA | PULSE |  | 10.00000 | 0.000000 | -------- | -------- | --------
975 | FQ050318() | HPM | COMPONNT | "DEBIT GAS CHAUDIERE #8" | "m3 " | " " | "GN " | " " | GN | 01 | 7 | 0 | 44 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT050318.PV | [12 empty] | EQA | PULSE |  | 10.00000 | 0.000000 | -------- | -------- | --------
1003 | FQ050319() | HPM | COMPONNT | "DEBIT GAS CHAUDIERE #9" | "m3 " | " " | "GN " | " " | GN | 01 | 7 | 0 | 45 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT050319.PV | [12 empty] | EQA | PULSE |  | 1.000000 | 0.000000 | -------- | -------- | --------
1070 | FQ006317() | HPM | COMPONNT | "DEBIT MAZOUT CHAUDIERE#7" | "KG " | " " | "C7 " | " " | C7 | 01 | 7 | 0 | 49 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FY006F317.PV | [12 empty] | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
1099 | FQ006318() | HPM | COMPONNT | "DEBIT MAZOUT CHAUDIERE#8" | "KG " | " " | "C8 " | " " | C8 | 01 | 7 | 0 | 50 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FY006F318.PV | [12 empty] | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 0.000000 | -------- | --------
1128 | FQ006319() | HPM | COMPONNT | "DEBIT MAZOUT CHAUDIERE#9" | "KG " | " " | "C9 " | " " | C9 | 01 | 7 | 0 | 51 |  |  | TOTALIZR | 1.000E08 | 0.000000 | D1 | 1.000E08 | 0.000000 | NOCLAMP |  | 0.000000 | [25 empty] | FT006319.PV | [12 empty] | EQB | ANALOG | HOURS | 1.000000 | 0.000000 | 1500.000 | -------- | --------
1465 | FY003317() | HPM | COMPONNT | "CONVERTIR ENG / % " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 1 |  |  | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FT003317.PV | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 " | FT003317.PVEUHI
1493 | FY004A317() | HPM | FULL | "SOMMATEUR " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 2 | -- | "----------------" | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FT004A317.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | EQC | [7 empty] | 4 | [5 empty] | FT004B317.PV | 1 | OFF | FT004C317.PV | FT004D317.PV | --------
1539 | FY004B317() | HPM | FULL | "CARACTERISATION AIR/GAZ " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 3 | -- | "----------------" | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 12 | 14.50000 | 7.000000 | 28.60000 | 15.00000 | 38.70000 | 22.00000 | 47.30000 | 29.00000 | 53.10000 | 34.00000 | 57.50000 | 39.00000 | 64.80000 | 45.00000 | 71.70000 | 51.00000 | 76.50000 | 54.00000 | 85.90000 | 62.00000 | 89.40000 | 66.00000 | FY004A317.PVCALC | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [20 empty] | 92.00000 | 70.00000 | 96.00000 | 75.00000
1604 | FY004C317() | HPM | FULL | "CARACTERISAT. AIR/MAZOUT" | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 4 | -- | "----------------" | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 12 | 20.00000 | 0.000000 | 26.50000 | 15.00000 | 28.80000 | 20.50000 | 32.20000 | 23.50000 | 36.40000 | 27.50000 | 41.10000 | 32.00000 | 46.30000 | 37.00000 | 55.10000 | 44.00000 | 63.70000 | 51.00000 | 71.10000 | 57.00000 | 78.60000 | 63.00000 | FY004A317.PVCALC | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [20 empty] | 85.10000 | 70.00000 | 90.50000 | 80.00000
1682 | FY004E317() | HPM | FULL | "DIVISEUR " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 5 | -- | "----------------" | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY004D317.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [8 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/(.9+(.002*P2)) " | AC080317.OP
1810 | FY004F317() | HPM | FULL | "LO SELECTEUR AIR/MAITRE " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 6 | -- | "----------------" | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY004E317.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | HIGH | ENABLE | EQB | [7 empty] | 2 | [5 empty] | HC310317.OP | 2 | OFF |  |  | --------
1906 | FY005A317() | HPM | COMPONNT | "CONVERTIR M3/H_MBTU/H " | "MBTU/h " | " " | " " | " " | C7 | 01 | 7 | 0 | 9 |  |  | CALCULTR | 400.0000 | 0.000000 | D1 | 440.0000 | -40.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FT005317.PV | [20 empty] | 3 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FT005317.PVEUHI |  |  | FFC005317.PVEUHI
1948 | FY005_006A317() | HPM | FULL | "SOMMATEUR MBTU/H " | "MBTU/h " | " " | " " | " " | C7 | 01 | 7 | 0 | 11 | -- | "----------------" | SUMMER | 400.0000 | 0.000000 | D1 | 480.0000 | -40.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY005A317.PVCALC | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | EMERGNCY | ENABLE | EQB |  |  | 1.000000 |  |  |  |  | 2 | 1.003000 | 1.006000 |  |  |  | FY006B317.PVCALC | [9 empty] | 0.000000
1993 | FY005_006B317() | HPM | COMPONNT | "CONVERTIR MBTU/H _ % " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 12 |  |  | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY005_006A317.PVCALC | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 " | FFC005317.PVEUHI
2103 | FY005B317() | HPM | COMPONNT | "CONVERTIR % _ MBTU/H " | "MBTU/h " | " " | " " | " " | C7 | 01 | 7 | 0 | 10 |  |  | CALCULTR | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY004F317.PVCALC | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*P2 " | FFC005317.PVEUHI
2131 | FY006B317() | HPM | COMPONNT | "CONVERTIR KG/H_MBTU/H " | "MBTU/h " | " " | " " | " " | C7 | 01 | 7 | 0 | 13 |  |  | CALCULTR | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY006A317.PV | [20 empty] | 3 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FT006317.PVEUHI |  |  | FFC006317.PVEUHI
2238 | FY004G317() | HPM | FULL | "HI SELECTEUR AIR/MAITRE " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 7 | -- | "----------------" | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY005_006B317.PVCALC | -- | NONE | NONE | 0 | 0 | ONE | -------- | 0.000000 | -------- | -------- | HIGH | ENABLE | EQA | [7 empty] | 3 | [5 empty] | HC310317.OP | 3 | OFF | FY004G317.PVLOTP |  | -------- | [5 empty] | LOW | CUTOUT | --------
2694 | FY004H317() | HPM | FULL | "CARACT. AIR BAS REGIME " | "% " | " " | " " | " " | C7 | 01 | 7 | 0 | 8 | -- | "----------------" | GENLIN | 100.0000 | 0.000000 | D1 | 750.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 2 | 0.000000 | 5.000000 | 15.00000 | 50.00000 | 30.00000 | 100.0000 | [16 empty] | PDZ013317.OP | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
3644 | FY006C317() | HPM | COMPONNT | "CONVERTIR % _ MBTU/H " | "MBTU/h " | " " | " " | " " | C7 | 01 | 7 | 0 | 14 |  |  | CALCULTR | 400.0000 | 0.000000 | D1 | 480.0000 | -80.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY004F317.PVCALC | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*P2 " | FFC006317.PVEUHI
4057 | FY004A318() | HPM | FULL | "CARACTERISATION AIR/GAZ " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 27 | -- | " " | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 9 | 15.50000 | 2.200000 | 31.00000 | 16.50000 | 35.00000 | 24.20000 | 44.00000 | 31.40000 | 53.00000 | 38.80000 | 60.00000 | 45.90000 | 72.00000 | 56.00000 | 80.00000 | 63.00000 | 91.00000 | 69.00000 | 99.00000 | 78.00000 |  |  | FT004318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
4116 | FY004B318() | HPM | FULL | "CARACTERISAT. AIR/MAZOUT" | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 28 | -- | "----------------" | GENLIN | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | 10 | 13.50000 | 9.621000 | 25.20000 | 18.52700 | 36.30000 | 28.37300 | 46.70000 | 36.32500 | 55.10000 | 47.50000 | 64.40000 | 56.25000 | 73.60000 | 62.50000 | 79.00000 | 67.00000 | 85.70000 | 71.80000 | 92.00000 | 76.83000 | 95.00000 | 81.25000 | FT004318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE
4190 | FY004D318() | HPM | FULL | "DIVISEUR " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 29 | -- | "----------------" | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY004C318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | [8 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/(.9+(.002*P2)) " | AC080318.OP
4367 | FY004E318() | HPM | FULL | "LO SELECTEUR AIR/MAITRE " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 30 | -- | "----------------" | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY004D318.PV | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | HIGH | ENABLE | EQB | [7 empty] | 2 | [5 empty] | HC310318.OP | 2 | OFF |  |  | --------
4411 | FY005A318() | HPM | COMPONNT | "CONVERTIR M3/H_MBTU/H " | "MBTU/h " | " " | " " | " " | C8 | 01 | 7 | 0 | 32 |  |  | CALCULTR | 320.0000 | 0.000000 | D1 | 384.0000 | -64.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FT005318.PV | [20 empty] | 3 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FT005318.PVEUHI |  |  | FFC005318.PVEUHI
4440 | FY005B318() | HPM | COMPONNT | "CONVERTIR % _ MBTU/H " | "MBTU/h " | " " | " " | " " | C8 | 01 | 7 | 0 | 33 |  |  | CALCULTR | 320.0000 | 0.000000 | D1 | 384.0000 | -64.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY004E318.PVCALC | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*P2 " | FFC005318.PVEUHI
4592 | FY005_006A318() | HPM | FULL | "SOMMATEUR MBTU/H " | "MBTU/h " | " " | " " | " " | C8 | 01 | 7 | 0 | 40 | -- | "----------------" | SUMMER | 320.0000 | 0.000000 | D1 | 384.0000 | -64.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY005A318.PVCALC | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | LOW | ENABLE | EQB |  |  | 1.000000 |  |  |  |  | 2 | 1.000000 | 1.000000 |  |  |  | FY006B318.PVCALC | [9 empty] | 0.000000
4637 | FY006B318() | HPM | COMPONNT | "CONVERTIR KG/H_MBTU/H " | "MBTU/h " | " " | " " | " " | C8 | 01 | 7 | 0 | 36 |  |  | CALCULTR | 320.0000 | 0.000000 | D1 | 384.0000 | -64.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY006A318.PV | [20 empty] | 3 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*P3 " | FT006318.PVEUHI |  |  | FFC006318.PVEUHI
4666 | FY005_006B318() | HPM | COMPONNT | "CONVERTIR MBTU/H _ % " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 41 |  |  | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY005_006A318.PVCALC | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 " | FFC005318.PVEUHI
4846 | FY006C318() | HPM | COMPONNT | "CONVERTIR % _ MBTU/H " | "MBTU/h " | " " | " " | " " | C8 | 01 | 7 | 0 | 37 |  |  | CALCULTR | 320.0000 | 0.000000 | D1 | 384.0000 | -64.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FY004E318.PVCALC | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/100*P2 " | FFC006318.PVEUHI
4874 | FY004F318() | HPM | FULL | "HI SELECTEUR AIR/MAITRE " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 31 | -- | "----------------" | HILOAVG | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP | ONLYAUTO | 0.000000 | -------- | 25 | [23 empty] | FY005_006B318.PVCALC | -- | NONE | NONE | 0 | 0 | ONE | -------- | -------- | -------- | -------- | HIGH | ENABLE | EQA | [7 empty] | 2 | [5 empty] | HC310318.OP | 2 | OFF |  |  | --------
5253 | FY003318() | HPM | COMPONNT | "CONVERTIR ENG / % " | "% " | " " | " " | " " | C8 | 01 | 7 | 0 | 42 |  |  | CALCULTR | 100.0000 | 0.000000 | D1 | 120.0000 | -20.0000 | NOCLAMP |  | 0.000000 | [25 empty] | FT003318.PV | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1/P2*100 " | FT003318.PVEUHI
6018 | FY005_006C317() | HPM | COMPONNT | "SURVEILLANCE AIR/COMBUS." | " " | " " | " " | " " | C7 | 01 | 7 | 0 | 15 |  |  | CALCULTR | 100.0000 | -100.000 | D1 | 100.0000 | -100.000 | NOCLAMP |  | 0.000000 | [25 empty] | FY004E317.PVCALC | [20 empty] | 3 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "(P1/100*P2)-P3 " | FFC006317.PVEUHI |  |  | FY005_006A317.PV
6123 | PDY013A317() | HPM | COMPONNT | "SOMM PRESSIODIFF AIR FOR" | "PO H2O " | " " | " " | " " | C7 | 01 | 7 | 0 | 21 |  |  | CALCULTR | 25.00000 | 0.000000 | D1 | 35.00000 | -2.50000 | NOCLAMP |  | 0.000000 | [25 empty] | PT013317.PV | [20 empty] | 2 | 0.000000 | 0.000000 | 0.000000 | 0.000000 | "P1-P2 " | PT014317.PV